## Cover (hidden)
YANBU
Export Refinery Project
PROCESS AUTOMATION SYSTEM (PAS)
Price Summary
| Doc No. 192-YER-PE-I35-0021 |  |  | GENERAL/BUSINESS CONFIDENTIAL - This document and the information herein contained are the confidential proprietary information of the Yanbu Export Refinery Company. Any disclosure to third parties, use, or reproduction without proper authorization is strictly prohibited.
| REV | DATE | ISSUED FOR |  | PREPARED BY | REVIEWED BY | APPROVED BY
| F1 | 2007-03-08 | Informal Engr. Interdiscipline Check |  | BA | RMS | TGA
| F2 | 2007-03-29 | Informal Review with Cient |  | BA | RMS | TGA
| F3 | 2007-04-25 | Issued for Client Approval |  | BA | RMS | TGA
Page: 1 of 19

## Technical Queries Register
| Project Name | Installation and commissioning of the new Sootblower PLCs and SCADA system on Unit 5, supply of cabling and retrofit of the changes made on unit 2, 4 and 6 for the period of one (1) year at Kendal Power Station.
| Customer Name | Eskom
| Bid Ref No. and dt | MPKEN10244GX
TECHNICAL QUERIES
TQ No. | TQ Dated | Reference Document No. | Section / Clause No. | Page No. | Bidders Queries | Clarifications from LBU / End Customer | Customer response received on | Query Status (Open / Closed)
1 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.1 | 4/42 | This project is for the replacement of the obsolete Sootblower Control System on unit 5 from the Modicon 884 PLC to the advanced Quantum PLC, with the same configurations that were implemented on Units 1 and 3.
2 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.1 | 4/42 | The replacement includes the refurbishment of the Mimic Panel which is the Operator’s interface with the field (plant) and installation of the new SCADA HMI. | We understand Mimic panel is being replaced bu Operator work station | Yes
3 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 4/42 | To be able to use data from the PI data historian to enable full automatic soot blow scheduling and automatic execution. | Protocol used to communicate with PI Historian | TCP/IP
4 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 4/42 | To install new pressure transmitters on both common ranges (air heater and lance or wall blowers), which will be supplied by the Employer | 1. Please provide qty of Pressure switches which is to be replaced by Pressure Transmitter (Supplied by Emplyer). If any new Transmitter to be erected. 2. Distance between Sootblower Panel and Field JB. | 1. Four pressure transmitters free-issues. 2. Pressure transmitters are installed on the plant, what is required is the installation of impulse lines.
5 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 5/42 | The decommissioning of the existing Sootblower PLC and mimic panels on Unit 5. | Old cable to retain so new sootblower panel shall be mounted in the same space. | Yes
6 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 5/42 | The supply and installation of all power cables (24VDC and 220VAC) required for the works. | We understand that input Power to the panel shall be 220VAC UPS. Please note that supply and installation of power cables shall be upto ABB supplied sootblower panel. | Noted
7 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 5/42 | The supply and installation of all cabling (UVG), junction boxes and any other Plant and Material required for routing the analogue ammeter signals from the Mimic panel to the PLC in the unit equipment room | We understand that the ammeter signals are available in existing MIMIC Panel (which is to be dismantled) and the signals are available in 4-20 mA. Please provide the qty of signals to consider. | 18 ammeter gauges
8 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 5/42 | The connection of the PLC and HMI to the nearest access point on the current Hirschmann network. All communication between the PLC, HMI and PI server shall be routed via the Hirschmann network. | We recoomend to have ABB's network for the PLC and HMI network. For connection to PI server, we recommend to have Firewall in between ABB and PI Server network. | We prefer that Unit 5 be configured as the other Units via the Hirschmann Network (TCP/IP) for Standardization.
9 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 6/42 | IOs | We have considered the IO channels as below 1. AI (4-20mA) - 48 Channels 2. Thermocouple - 16 Channels 3. Digital Input (Non SOE) - 320 Channels 4. Digital Output - 288 Channels | Noted
10 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 6/42 | The Contractor removes the old Sootblower System and installs and commissions the new Sootblower System without disrupting the Unit sootblowing sequence. | To be discussed in detail | Yes, during the detail design phase.
11 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 6/42 | ll the changes to hardware, software and documentation that are to be implemented on the units 5 must be retrofitted back onto units 1, 2, 3, 4 & 6. | Unit 1 and 3 is already supplied by other. The RFQ is for Unit-2,4,5 & 6. | Noted
12 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 6/42 | The Computer‘s Operating System of Windows 7 must be 32 bits for all units. | The OS shall be Windows 10 or Windows server 2019. | Noted
13 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 6/42 | The re-drawn 160 P&ID drawings to be supplied for all six units. | The RFQ is for Unit-2,4,5 & 6. Please provide the qty of P&ID of Sootblower systen for these units. | Noted
14 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 7/42 | To separate charging-up of the system on Air heaters and Lance blowers on the local and manual modes. | from which location operator will operate in Local mode. | Local modes is when the operator operates physically in the plant. Manual/remote is when charging is done from the HMI
15 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 1.2 | 7/42 | SCADA failure: hardwire reset button to cancel the alarm, emergency shutdown (PLC shutdown.) | An emergency PB can be provided to retract all the sootblowers in case of HMI Failure. | Noted
16 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 2.13 | 14/42 | Training provided by the Contractor is directly applicable to Kendal Power Station’s new Sootblower System hardware and software components.
17 | 2022-05-18 | C3 1 ECC3 Employers Works Information | 4.2.3 | 24/42 | All Plant and Material for the Unit and Simulator HMI and network are provided by the Contractor. | Is Simulator in scope. Need more details and scope. | No. Simulator not part of the scope.
18 | 2022-05-18 | C3 1 ECC3 Employers Works Information |  |  | General Query | Please provide sootblower wiring / logic diagrams. | Wiring/Logic will be issued to the suitable supplier during the Detail Design phase.
19 | 2022-05-18 | C3 1 ECC3 Employers Works Information |  |  | General Query | How many server/OWS to be considered | 1 Operator station with 2 screens.
20 | 2022-05-24 | Clarifiaction meeting |  |  | The supply of a SCADA Software Licence to cater for 5000 tags. | Will the software license be required on as a bill of quantities (BOQ) items. | Yes, it will be included in the revised BOQ.
21 | 2022-05-24 | Clarifiaction meeting |  |  | General Query | What is the full wod of the acronym PG Unit | Programmable Unit
22 | 2022-05-24 | Clarifiaction meeting |  |  | General Query | Will the pressure transmitters to replace the swtiches be supplied by the Customer(Kendal P.S) | Yes, four pressure transmitters.
23 | 2022-05-30 | Clarifiaction meeting |  |  | General Query | 1. Please confirm the number of: o Citect SCADA Control Clients o Citect SCADA View-only Clients | Only two SCADA control clients required
24 | 2022-05-30 | Clarifiaction meeting |  |  | General Query | 2. Do you require redundancy? | No
25 | 2022-05-30 | Clarifiaction meeting |  |  | General Query | Installation of new Sootblowing SCADA HMI that will communicate with the newly installed PLC and with the necessary interfaces to the PI data historian. To be able to use data from the PI data historian to enable full automatic soot blow scheduling and automatic execution. Please confirm if you intend sending the data to PI directly from the PLC or via the SCADA as this would impact the drivers needed. (for information, Kendal’s PI SRP has not been renewed which may impact the delivery of the required drivers) | The data shall be comminucated from the Citect SCADA to the PI-Historian via the Hirschmann netwrok (TCP/IP).

## Common (hidden)
YANBU EXPORT REFINERY PROJECT
PAS PRICE SUMMARY
Document No. 192-YER-PE-I35-0021
Revision No.: F3
Issue Date: 25 April 2007
MATERIAL COST SUMMARY