keith

NEC3 Term Service Contract (TSC3)

| Between | ESKOM HOLDINGS LIMITED (Reg No. 2002/015527/06) |  |
| --- | --- | --- |
| and | (Reg No. ………………………) |  |
| for | MAINTENANCE AND REPAIRS OF DEMINERALISED TRAIN VESSELS AND CONDENSATE POLISHING REGENERATION (CPR) VESSELS. |  |
| Contents: |  | No of pages |
| Part C1 | Agreements & Contract Data | 3-16 |
| Part C2 | Pricing Data | C.21 |
| Part C3 | Scope of Work | C.31 |
| CONTRACT No. |  |  |

PART C1:	AGREEMENTS & CONTRACT DATA

| Contents: |  | No of pages |
| --- | --- | --- |
| C1.1 | Form of Offer and Acceptance | 3 |
| C1.2a | Contract Data provided by the Employer | 6 |
| C1.2b | Contract Data provided by the Contractor | 16 |

C1.1 Form of Offer & Acceptance

## Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Maintenance and repairs of Demineralized train vessels and Condensate Polishing Regeneration (CPR) vessels

The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data.

Delete the row for the Options which do not apply

| Options A | The offered total of the Prices exclusive of VAT is | AS PER PRICE LIST RATES |
| --- | --- | --- |
|  | Value Added Tax @ 14% is | AS PER PRICE LIST RATES |
|  | The offered total of the amount due inclusive of VAT is | AS PER PRICE LIST RATES |
|  | (in words N/A |  |

This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| For the tenderer: |  |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |
| Tenderer’s CIDB registration number: |  |  |  |  |

## Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in:

Part C1		Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2		Pricing Data

Part C3		Scope of Work: Service Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed original copy of this document, including the Schedule of Deviations (if any).

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) | T Ndimande |  |  |  |
| Capacity | Procurement Manager |  |  |  |
| for the Employer | ESKOM LETHABO POWER STATION PRIVATE BAG 415 VEREENIGING 1935 |  |  |  |
| Name & signature of witness |  |  | Date |  |

Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

## Schedule of Deviations to be completed by the Employer prior to contract award

Note:

- This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.

- The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

- A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

| No. | Subject | Details |
| --- | --- | --- |
| 1 | [●] | [●] |
| 2 | [●] | [●] |
| 3 | [●] | [●] |
| 4 | [●] | [●] |
| 5 | [●] | [●] |
| 6 | [●] | [●] |
| 7 | [●] | [●] |

By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement.

|  | #### For the tenderer: |  | #### For the Employer |
| --- | --- | --- | --- |
| Signature |  |  |  |
| Name |  |  | T Ndimande |
| Capacity |  |  | Procurement Manager |
| On behalf of | (Insert name and address of organisation) |  | (Insert name and address of organisation) ESKOM LETHABO POWER STATION PRIVATE BAG 415 VEREENIGING 1935 |
| Name & signature of witness |  |  |  |
| Date |  |  |  |

C1.2 TSC3 Contract Data

# Part one - Data provided by the Employer

| Clause |  | ## Statement | ## Data |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 |  | ## General |  |  |  |
|  |  | The conditions of contract are the core clauses and the clauses for main Option: |  |  |  |
|  |  |  | A: Priced contract with price list |  |  |
|  |  | dispute resolution Option | W1: Dispute resolution procedure |  |  |
|  |  | and secondary Options |  |  |  |
|  |  |  | X1: Price adjustment for inflation |  |  |
|  |  |  | X2 Changes in the law |  |  |
|  |  |  | X17: Low service damages |  |  |
|  |  |  | X18: Limitation of liability |  |  |
|  |  |  | X19: Task Order X20: Key performance indicators |  |  |
|  |  |  | Z: Additional conditions of contract |  |  |
|  |  | of the NEC3 Term Service Contract (June 2005) |  |  |  |
| 10.1 |  | The Employer is (name): | Eskom Holdings Limited (reg no: 2002/015527/06), a juristic person incorporated in terms of the company laws of the Republic of South Africa |  |  |
|  |  | Address | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |  |
|  |  | Tel No. | (016) 457 5700 |  |  |
|  |  | Fax No. | 086 661 7624 |  |  |
| 10.1 |  | The Service Manager is (name): | Mr P Mohohlo |  |  |
|  |  | Address | Lethabo Power Station Deneysville Rd Viljoensdrift |  |  |
|  |  | Tel | (016) 457-5096 |  |  |
|  |  | Fax | 016 457 5381 |  |  |
|  |  | e-mail | Budelil@eskom.co.za |  |  |
| 11.2(2) |  | The Affected Property is | Water Treatment Plant (WTP) |  |  |
| 11.2(13) |  | The service is | MAINTENANCE AND REPAIRS OF DEMINERALISED TRAIN VESSELS AND CONDENSATE POLISHING REGENERATION (CPR) VESSELS |  |  |
| 11.2(14) |  | The following matters will be included in the Risk Register | NONE |  |  |
| 11.2(15) |  | The Service Information is in | Part 3: Scope of Work and all documents and drawings to which it makes reference. |  |  |
| 12.2 |  | The law of the contract is the law of | the Republic of South Africa |  |  |
| 13.1 |  | The language of this contract is | English |  |  |
| 13.3 |  | The period for reply is | 2 days |  |  |
| ## 2 |  | ## The Contractor’s main responsibilities | (If the optional statement for this section is not used, no data will be required for this section) |  |  |
| 21.1 |  | The Contractor submits a first plan for acceptance within | 2 weeks of the Contract Date |  |  |
| ## 3 |  | ## Time |  |  |  |
| 30.1 |  | The starting date is. | 01 January 2020 |  |  |
| 30.1 |  | The service period is | 31 December 2023 (3 years) |  |  |
| ## 4 |  | ## Testing and defects | ## No data is required for this section of the conditions of contract. |  |  |
| ## 5 |  | ## Payment |  |  |  |
| 50.1 |  | The assessment interval is | Between the 25th day of each successive month. |  |  |
| 51.1 |  | The currency of this contract is the | South African Rand |  |  |
| 51.2 |  | The period within which payments are made is | 4 Weeks. |  |  |
| 51.4 |  | The interest rate is | (i) zero percent above the publicly quoted prime rate of interest (calculated on a 365 day year) charged by from time to time by the Standard Bank of South Africa (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and (ii) the LIBOR rate applicable at the time for amounts due in other currencies. LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter (and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove. |  |  |
| ## 6 |  | ## Compensation events | (If the optional statement for this section is not used, no data will be required for this section) |  |  |
|  |  | These are additional compensation events: | 1 | [●] |  |
|  |  |  | 2 | [●] |  |
| ## 7 |  | ## Use of Equipment Plant and Materials | ## No data is required for this section of the conditions of contract. |  |  |
| ## 8 |  | ## Risks and insurance |  |  |  |
| 80.1 |  | These are additional Employer's risks | 1. [●] |  |  |
|  |  |  | 2. [●] |  |  |
|  |  |  | 3. [●] |  |  |
| 83.1 |  | The Employer provides these insurances from the Insurance Table | as stated for “Format TSC3” available on http://www.eskom.co.za/live/content.php?Item_ID=9248 (See Annexure A for basic guidance). |  |  |
| 83.1 |  | The Employer provides these additional insurances | as stated for “Format TSC3” available on http://www.eskom.co.za/live/content.php?Item_ID=9248 (See Annexure A for basic guidance) |  |  |
| 83.1 |  | The minimum amount of cover for insurance against loss and damage caused by the Contractor to the Employer’s property is | the amount of the deductibles relevant to the event described in the “Format TSC3” insurance policy available on http://www.eskom.co.za/live/content.php?Item_ID=9248 |  |  |
| 83.1 |  | The minimum amount of cover for loss of or damage to Plant and Materials provided by the Employer is: | the amount of the deductibles relevant to the event described in the “Format TSC3” insurance policy available on http://www.eskom.co.za/live/content.php?Item_ID=9248 |  |  |
| 83.1 |  | The minimum amount of cover for insurance in respect of loss of or damage to property (except the Employer’s property, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) arising from or in connection with the Contractor’s Providing the Service for any one event is: | Whatever the Contractor deems necessary in addition to that provided by the Employer. |  |  |
| 83.1 |  | The minimum limit of indemnity for insurance in respect of death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract for any one event is: | As prescribed by the Compensation for Occupational Injuries and Diseases Act No. 130 of 1993 and the Contractor’s common law liability for people falling outside the scope of the Act with a limit of Indemnity of not less than R500 000 (Five hundred thousand Rands).. |  |  |
| ## 9 |  | ## Termination | There is no Contract Data required for this section of the conditions of contract. |  |  |
| ## 10 |  | ## Data for main Option clause |  |  |  |
| A |  | Priced contract with price list |  |  |  |
| 20.5 |  | The Contractor prepares forecasts of the final total of the Prices for the whole of the service at intervals no longer than | 2 weeks. |  |  |
| E |  | Cost reimbursable contract |  |  |  |
| ## 11 |  | ## Data for Option W1 |  |  |  |
| W1.1 |  | The Adjudicator is (Name) | Either State the name of the person selected & complete the contact details below Or, state the person selected from the Eskom Panel of Adjudicators listed in Annexure B to this Contract Data by the Party intending to refer a dispute to him. |  |  |
|  |  | Address | [●] |  |  |
|  |  | Tel No. | [●] |  |  |
|  |  | Fax No. | [●] |  |  |
|  |  | e-mail | [●] |  |  |
| W1.2(3) |  | The Adjudicator nominating body is: | the Chairman of the Joint Civils Division of the South African Institution of Civil Engineering. (See www.jointcivils.co.za) |  |  |
| W1.4(2) |  | The tribunal is: | arbitration |  |  |
| W1.4(5) |  | The arbitration procedure is | the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body. |  |  |
|  |  | The place where arbitration is to be held is | [●] South Africa |  |  |
|  |  | The person or organisation who will choose an arbitrator - if the Parties cannot agree a choice or - if the arbitration procedure does not state who selects an arbitrator, is | the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body. |  |  |
| ## 12 |  | ## Data for secondary Option clauses |  |  |  |
| X1 |  | Price adjustment for inflation |  |  |  |
| X1.1 |  | The base date for indices is | [●] The prices offered are in Rand and are fixed and firm for the first year thereafter subject to |  |  |
| X2 |  | Changes in the law | No data is required for this Option |  |  |
| X17 |  | Low service damages |  |  |  |
| X17.1 |  | The service level table is in | [●] |  |  |
| X18 |  | Limitation of liability |  |  |  |
| X18.1 |  | The Contractor’s liability to the Employer for indirect or consequential loss is limited to | R0.0 (zero Rand) |  |  |
| X18.2 |  | For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to | the amount of the deductibles relevant to the event described in the “Format TSC3” insurance policy available on http://www.eskom.co.za/live/content.php?Item_ID=9248 |  |  |
| X18.3 |  | The Contractor’s liability for Defects due to his design of an item of Equipment is limited to | The greater of the total of the Prices at the Contract Date and the amounts excluded and unrecoverable from the Employer’s insurance (other than the resulting physical damage to the Employer’s property which is not excluded) plus the applicable deductibles in the Employer’s assets and works / maintenance policies available on http://www.eskom.co.za/live/content.php?Item_ID=9248 |  |  |
| X18.4 |  | The Contractor’s total liability to the Employer, for all matters arising under or in connection with this contract, other than the excluded matters, is limited to | the total of the Prices other than for the additional excluded matters. The Contractor’s total liability for the additional excluded matters is not limited. The additional excluded matters are amounts for which the Contractor is liable under this contract for Defects due to his design, plan and specification, Defects due to manufacture and fabrication outside the Affected Property, loss of or damage to property (other than the Employer’s property, Plant and Materials), death of or injury to a person and infringement of an intellectual property right. |  |  |
| X18.5 |  | The end of liability date is | 12 months after the end of the service period. |  |  |
| X19 |  | Task Order |  |  |  |
| X19.5 |  | The Contractor submits a Task Order programme to the Service Manager within | 2 days of receiving the Task Order |  |  |
| Z |  | The additional conditions of contract are | Z1 to Z11 always apply. |  |  |
| Z1 | Cession delegation and assignment |  |  |  |  |
| Z1.1 | The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer. |  |  |  |  |
| Z1.2 | Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry and the Electricity Distribution Industry. |  |  |  |  |
| Z2 | Joint ventures |  |  |  |  |
| Z2.1 | If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract. |  |  |  |  |
| Z2.2 | Unless already notified to the Employer, the persons or organisations notify the Service Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf. |  |  |  |  |
| Z2.3 | The Contractor does not substantially alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing. |  |  |  |  |
| Z3 |  | Change of Broad Based Black Economic Empowerment (B-BBEE) status |  |  |  |
| Z3.1 |  | Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change. |  |  |  |
| Z3.2 |  | The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Service Manager within thirty days of the notification or as otherwise instructed by the Service Manager. |  |  |  |
| Z3.3 |  | Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Works. |  |  |  |
| Z3.4 |  | Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P4 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93. |  |  |  |
| Z4 | Ethics |  |  |  |  |
| Z4.1 | Any offer, payment, consideration, or benefit of any kind made by the Contractor, which constitutes or could be construed either directly or indirectly as an illegal or corrupt practice, as an inducement or reward for the award or in execution of this contract constitutes grounds for terminating the Contractor’s obligation to Provide the Service or taking any other action as appropriate against the Contractor (including civil or criminal action). |  |  |  |  |
| Z4.2 | The Employer may terminate the Contractor’s obligation to Provide the Service if the Contractor (or any member of the Contractor where the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations) is found guilty by a competent court, administrative or regulatory body of participating in illegal or corrupt practices. Such practices include making of offers, payments, considerations, or benefits of any kind or otherwise, whether in connection with any procurement process or contract with the Employer or other people or organisations and including in circumstances where the Contractor or any such member is removed from the an approved vendor data base of the Employer as a consequence of such practice. |  |  |  |  |
| Z4.3 | Notwithstanding the provisions of core clause 90.2, the procedures on termination in terms of this clause are P1, P2 and P4 as stated in the core clause 92 and the amount due is A1 and A3 as stated in core clause 93. |  |  |  |  |
| Z5 | Confidentiality |  |  |  |  |
| Z5.1 | The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time). Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient. |  |  |  |  |
| Z5.2 | If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Service Manager. |  |  |  |  |
| Z5.3 | In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure. In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed. |  |  |  |  |
| Z5.4 | The taking of images (whether photographs, video footage or otherwise) of the Affected Property or any portion thereof, in the course of Providing the Service and after the end of the service period, requires the prior written consent of the Service Manager. All rights in and to all such images vests exclusively in the Employer. |  |  |  |  |
| Z5.5 | The Contractor ensures that all his subcontractors abide by the undertakings in this clause. |  |  |  |  |
| Z6 | Waiver and estoppel: Add to core clause 12.3: |  |  |  |  |
| Z6.1 | Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Service Manager or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing. |  |  |  |  |
| Z7 |  | Health, safety and the environment: Add to core clause 27.4 |  |  |  |
| Z7.1 |  | The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the service. Without limitation the Contractor: accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2003 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Affected Property; warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of the service; and undertakes, in and about the execution of the service, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |  |
| Z7.2 |  | The Contractor, in and about the execution of the service, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |  |
| Z8 | Provision of a Tax Invoice and interest. Add to core clause 51 |  |  |  |  |
| Z8.1 | Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Service Information, showing the amount due for payment equal to that stated in the payment certificate. |  |  |  |  |
| Z8.2 | If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice. Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made. |  |  |  |  |
| Z8.3 | The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment. |  |  |  |  |
| Z9 | Notifying compensation events |  |  |  |  |
| Z9.1 | Delete from the last sentence in core clause 61.3, “unless the Service Manager should have notified the event to the Contractor but did not”. |  |  |  |  |
| Z10 | Employer’s limitation of liability |  |  |  |  |
| Z10.1 | The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand) |  |  |  |  |
| Z10.2 | The Contractor’s entitlement under the indemnity in 82.1 is provided for in 60.1(12) and the Employer’s liability under the indemnity is limited to compensation as provided for under the compensation events stated in this contract. |  |  |  |  |
| Z11 | Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it": |  |  |  |  |
| Z11.1 | or had a judicial management order granted against it. |  |  |  |  |

# Annexure A:	Insurance provided by the Employer

These notes are provided as guidance to tendering contractors and the Contractor about the insurance provided by the Employer. Details of the insurance itself are available from the internet web link given below.

- Services provided in a TSC3 contract could include some element of construction or refurbishment as well as a continuous maintenance or operational service activity.  If an event occurs which causes loss or damage, a claim could be made either against the Employer’s “works” type policy which may be in place for the Employer’s portion of the Affected Property concerned or against the Employer’s assets policy which may be in place for the Employer’s portion of the Affected Property concerned, or both.

- The cover provided and the deductibles under the works policy are different to those under the assets policy.   Each policy has a range of applicable deductibles depending on the location of the Affected Property and the nature of the insurable event.

- The Contractor is required in terms of Contract Data for clause 83 to provide cover for the deductibles in the insurance provided by the Employer.  This can be provided from his own resources on a ‘self insured’ basis or obtained by him from his own insurers.   In order to assess the extent of this cover, tendering contractors and their brokers should consult the internet web link given below and scroll to ‘Format TSC3’ to establish both the cover and the deductibles in relation to the service provided in terms of this contract.

- Tendering contractors should note that cover provided by the Employer is only per the policies available on the internet web link listed below and may not be the cover required by the tendering contractor or as intended by each of the listed insurances in the left hand column of the Insurance Table in clause 83.2.  In terms of clause 83.1 “the Contractor provides the insurances stated in the Insurance Table except any insurance which the Employer is to provide”.  Hence the Contractor provides insurance which the Employer does not provide and in cases where the Employer does provide insurance the Contractor insures for the difference between what the Insurance Table requires and what the Employer provides.

- If Marine Insurance is required the Contractor needs to obtain a copy of the latest edition of Eskom’s Marine Policies Procedures found at internet website given below.

- Further information and full details of all Eskom provided policies and procedures may be obtained from:

http://www.eskom.co.za/live/content.php?Item_ID=9248

Annexure B:	The Employer’s Panel of Adjudicators

The following persons listed in alphabetical order of their surname have indicated their willingness to be included in the Eskom Panel of Adjudicators.  Their CV’s may be obtained by using the contact details provided.

| Name | Location | Contact details (phone & e mail) |
| --- | --- | --- |
| Nigel ANDREWS | Gauteng | +27 11 836-6760 nigela@quoin.net |
| Andrew BAIRD | Gauteng | +27 11 803 3008 andrewbaird@ecsconsult.co.za |
| Christopher BINNINGTON | Gauteng | +27 11 888-6141 cdb@bca.co.za |
| Peter HIGGINS | UK | +44 1293 873 868 peterhiggins@pdconsult.co.uk |
| Bruce LEECH | Gauteng | +27 11 290 4000 leech@counsel.co.za |
| Nigel NILEN | Gauteng | +27 11 465 3601; nilences@global.co.za |
| Robert St. LEGER | Cape Town | +27 21 794 7488 bobst@iafrica.com |
| Peter THURLOW | Gauteng | +27 11 787 6226 info@thurlowassoc.com |

Information about the Panel and appointment of the selected Adjudicator is in _________

C1.2 Contract Data

# Part two - Data provided by the Contractor

| ## Clause | ## Statement | ## Data |
| --- | --- | --- |
| 10.1 | The Contractor is (Name): |  |
|  | Address |  |
|  | Tel No. |  |
|  | Fax No. |  |
| 11.2(8) | The direct fee percentage is | 0% |
|  | The subcontracted fee percentage is | 0% |
| 11.2(14) | The following matters will be included in the Risk Register |  |
| 11.2(15) | The Service Information for the Contractor’s plan is in: |  |
| 21.1 | The plan identified in the Contract Data is contained in: |  |
| 24.1 | The key persons are: |  |
|  | 1 Name: |  |
|  | Job: |  |
|  | Responsibilities: |  |
|  | Qualifications: |  |
|  | Experience: |  |
|  | 2 Name: |  |
|  | Job |  |
|  | Responsibilities: |  |
|  | Qualifications: |  |
|  | Experience: |  |
|  |  | CV's (and further key person's data including CVs) . |
| A | Priced contract with price list |  |
| 11.2(12) | The price list is in | C.21 |
| 11.2(19) | The tendered total of the Prices is | R |

Part 2: Pricing Data

TSC3 Option A

| Document reference | Title | No of pages |
| --- | --- | --- |
| C2.1 | Pricing assumptions: Option A | 2 |
| C2.2 | The price list | 3 |

C2.1 Pricing assumptions: Option A

# The conditions of contract

## How work is priced and assessed for payment

Clause 11 in NEC3 Term Service Contract, June 2005 (TSC3) core clauses and Option A states:

| Identified and defined terms | 11 11.2 | (12) The Price List is the price list unless later changed in accordance with this contract. |
| --- | --- | --- |
|  |  | (17) The Price for Services Provided to Date is the total of the Price for each lump sum item in the Price List which the Contractor has completed and where a quantity is stated for an item in the Price List, an amount calculated by multiplying the quantity which the Contractor has completed by the rate. |
|  |  | (19) The Prices are the amounts stated in the Price column of the Price List. Where a quantity is stated for an item in the Price List, the Price is calculated by multiplying the quantity by the rate. |

This confirms that Option A is a priced contract where the Prices are derived from a list of items of service which can be priced as lump sums or as expected quantities of service multiplied by a rate or a mix of both.

## Function of the Price List

Clause 54.1 in Option A states: “Information in the Price List is not Service Information”.  This confirms that instructions to do work or how it is to be done are not included in the Price List but in the Service Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Service in accordance with the Service Information”. Hence the Contractor does not Provide the Service in accordance with the Price List.   The Price List is only a pricing document.

## Link to the Contractor’s plan

Clause 21.4 states “The Contractor provides information which shows how each item description on the Price List relates to the operations on each plan which he submits for acceptance”.  Hence when compiling the price list, the tendering contractor needs to develop his first clause 21.2 plan in such a way that operations shown on it can be priced in the price list  and result in a satisfactory cash flow in terms of clause 11.2(17).

## Preparing the price list

It will be assumed that the tendering contractor has read Pages 14, 15 and 73 of the TSC3 Guidance Notes before preparing the price list.  Items in the price list may have been inserted by the Employer and the tendering contractor should insert any additional items which he considers necessary.  Whichever party provides the items in the price list the total of the Prices is assumed to be fully inclusive of everything necessary to Provide the Service as described at the time of entering into this contract.

      - As the Contractor has an obligation to correct Defects (core clause 42.1) and there is no compensation event for this unless the Defect was due to an Employer’s risk, the lump sum Prices and rates must also include for the correction of Defects.

      - If the Contractor has decided not to identify a particular item in the price list at the time of tender the cost to the Contractor of doing the work must be included in, or spread across, the other Prices and rates in the price list in order to fulfil the obligation to complete the service for the tendered total of the Prices.

      - There is no adjustment to lump sum prices in the price list if the amount, or quantity, of work within that lump sum item of service later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the Prices is as a result of a compensation event. See Clause 60.1.

      - Hence the Prices and rates tendered by the Contractor in the price list are inclusive of everything necessary and incidental to Providing the Service in accordance with the Service Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk.

      - The Contractor does not have to allow in his Prices and rates for matters that may arise as a result of a compensation event.  It should be noted that the list of compensation events includes those arising as a result of an Employer's risk event listed in core clause 80.1.

## Format of the price list

(From page 73 of the TSC3 Guidance Notes)

Entries in the first four columns in the price list in section C2.2 are made either by the Employer or the tendering contractor.

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering contractor enters the amount in the Price column only, the Unit, Expected Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for an item of work which is the rate for the work multiplied by the quantity completed, the tendering contractor enters the rate which is then multiplied by the Expected Quantity to produce the Price, which is also entered.

If the Contractor is to be paid a Price for an item proportional to the length of time for which a service is provided, a unit of time is stated in the Unit column and the expected length of time (as a quantity of the stated units of time) is stated in the Expected Quantity column.

C2.2 the price list

| Activity Description | Unit | Qty (total) | Rands (each) | Rands (total) |
| --- | --- | --- | --- | --- |
| Site Establishment (considering weather conditions and storage). | Sum | 1 |  |  |
| Compilation & Supply of Safety File prior to commencement of project. | Sum | 1 |  |  |
| Rubber lining of flat surfaces (vessel shell, excluding dome for full base recast), support beams, brackets, nozzles and manhole covers, including: Surface preparation (Grinding, stripping, blasting and lining) (including all tools, labour, materials, etc. required). | m2 | 80 |  |  |
| Rubber lining of nozzle/spool pieces (incl. Surface preparation (Grinding, stripping, blasting and lining) (including all tools, labour, materials etc. required). |  |  |  |  |
| 80 NB | m | 2 |  |  |
| 100 NB | m | 2 |  |  |
| 150 NB | m | 2 |  |  |
| 200 NB | m | 2 |  |  |
| Supply and install injection laterals as per SOW | ea | 40 |  |  |
| Supply and install Set of Effluent laterals as per SOW | ea | 4 |  |  |
| Supply and install Effluent laterals with wound cloth as per SOW | ea | 10 |  |  |
| Supply and install Effluent laterals with stainless steel fine mesh as per SOW | ea | 10 |  |  |
| Supply and install Mixed Bed Vessel Floor nozzles | ea | 20 |  |  |
| Ring repair of Tekapor floor (including all tools, labour, materials etc. required) | ea | 6 |  |  |
| Casting of new floor including rubber lining, (incl. removal of old base, stripping, grinding, blasting) and lateral system as per SOW (including all tools, labour, materials, etc. required). | Per vessel Volume approx. 0.5m3 | 9 |  |  |
| Supply of stainless steel clamps | ea | 50 |  |  |
| Supply of stainless steel bolts | ea | 50 |  |  |
| Supply of stainless steel nuts | ea | 50 |  |  |
| Supply of stainless steel washers | ea | 50 |  |  |
| Plastic welding of header as per SOW (including materials, equipment and labour). | mm | 1000 |  |  |
| Pre-Inspection as per SOW (including pre-spark test of vessel) | Per vessel | 15 vessels |  |  |
| NDT of vessels (spark test, hardness test, blasting profile) | Per vessel | 15 vessels |  |  |
| Other* | Sum |  |  |  |

NOTE: The detail requirements of activities specified on the price list above if found under scope of work, which detailed specific requirements. Please ensure you read the table activities and the detail of such an activity under scope section when pricing.

___________________________			___________________			________

Name							Signature				Date

Part 3: Scope of Work

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C3.1 | Employer’s Service Information | 2 |
| C3.2 | Contractor’s Service Information (insert at award stage or delete if not applicable) |  |
|  | Total number of pages |  |

C3.1: Employer’s service Information

Contents

Part 3: Scope of Work……………………………………………………………………………………….	…………5

C3.1: Employer’s service Information……………………………………………………………………………........5

1	Description of the service……………………………………………………………………………………..5

1.1	Executive overview	5

1.2	Employer’s requirements for the service	8

1.3	Interpretation and terminology	8

2	Management strategy and start up………………………………………………………………………….8

2.1	The Contractor’s plan for the service	8

2.2	Management meetings	9

2.3	Contractor’s management, supervision and key people	9

2.4	Provision of bonds and guarantees	9

2.5	Documentation control	9

2.6	Invoicing and payment	10

2.7	Contract change management	10

2.8	Records of Defined Cost to be kept by the Contractor	10

2.9	Insurance provided by the Employer	10

2.10	Training workshops and technology transfer	11

2.11	Design and supply of Equipment	11

2.12.1	Equipment……………………………………………………………………………………………………. 11

2.12.2	Information and other things……………………………………………………………………………….. 11

2.13	Management of work done by Task Order	11

3	Health and safety, the environment and quality assurance…………………………………….………..12

3.1	Health and safety risk management	12

3.2	Environmental constraints and management	16

3.3	Quality assurance requirements	16

4	Procurement………………………………………………………………………………………………......16

4.1	People	17

4.1.1	Minimum requirements of people employed……………….………………………………….....17

4.1.2	BBBEE and preferencing scheme………………………………………….……………………..17

1.3	Accelerated Shared Growth Initiative – South Africa (ASGI-SA)……………………………….……….18

4.2	Subcontracting	28

4.2.1	Preferred subcontractors……………………………………………………………….…………..18

4.2.2	Subcontract documentation, and assessment of subcontract tenders………………….…….18

4.2.3	Limitations on subcontracting…………………………………………………………..………….18

4.2.4	Attendance on subcontractors………………………………………………………….………….18	Error: Reference source not found

4.3	Plant and Materials	18

4.3.1	Specifications………………………………………………………………………………………..18

4.3.2	Correction of defects………………………………………………………………………………..18

4.3.3	Contractor’s procurement of Plant and Materials………………………………………………..19

4.3.4	Tests and inspections before delivery…………………………………………………………….19

4.3.5	Plant & Materials provided “free issue” by the Employer……………………………………….19

5	Working on the Affected Property……………………………………………………… ………………….19

5.1	Employer’s site entry and security control, permits, and site regulations	19

5.2	People restrictions, hours of work, conduct and records	19

5.3	Health and safety facilities on the Affected Property	20

5.4	Environmental controls, fauna & flora	20

5.5	Cooperating with and obtaining acceptance of Others	22

5.6	Records of Contractor’s Equipment	22

5.7	Equipment provided by the Employer	22

5.8	Site services and facilities	23

5.8.1	Provided by the Employer………………………………………………………………………….23

5.8.2	Provided by the Contractor……………………………………………………………………….. 23

5.9	Control of noise, dust, water and waste	26

5.10	Hook ups to existing works	27

5.11	Tests and inspections	27

5.11.1	Description of tests and inspections………………………………………………………………28

5.11.2	Materials facilities and samples for tests and inspections…...............……………..…..……..28

6	List of drawings………………………………………………………………………………..……………..	28

6.1	Drawings issued by the Employer……………………………….………………………………………….…...28

7	Site procedures……………………………………………….……………………………….……………...29

7.1	Permit to Work System …………….…………………..…………………………………………………….…..29

7.2	Safety Induction Course……….……………………….…………………………………………………….…..29

7.3	IBI Awareness Techniques …...………………….……………………………………………………………...30

7.4	Transportation of passengers: open LDV’s ……….…………………………………………………….……..30

7.5	Eskom Life Saving Rules …………………..……….……………………………………………………….…..30

7.6	Local Safety Procedures……….…………………….………………………………………………………..…31

7.7	Incidents / Accidents………………………………….……………………………………………….…………..31

7.8	Fire Prevention……….…………………………………….…………………………………………….………..31

7.9	Protective Equipment and Clothing……………..….…………………………………………….……………..31

7.10 Inspection of Equipment……………………..….…………………………………….…………………….…..31

7.11 Documentation……………………..….………………………………………………………………………....31

# Description of the service

The Works comprises of all activities necessary for the provision of a fully functional system that meets the Employer’s requirements. The scope includes the maintenance repairs required on the:

- Demineralised train 1, 2 and 3 vessels namely the Cation Exchange Vessel, Weak Base Anion Exchange Vessel, Strong Base Anion Exchange Vessel and Mixed Bed Vessel;

- Condensate Polishing Regeneration (CPR) vessels 10, 20, 30 namely the CPR Cation, Anion  and Resin storage Vessels;

At the West Water Treatment Plant at Lethabo Power Station inside the Water Treatment Building until complete refurbishment of the systems are complete. The repairs will be on an as and when required basis once a failure has been detected on a vessel.

Drawings

- 0.63/01849.02 General Arrangement of Cation Vessel

- 0.63/04687 rev 01 and 02 Cation Bottom Regenerant Lateral Details

- 0.63/04688 rev 01 and 02 Cation Regenerant Collector Details

- 0.63/01851.02 General Arrangement of Weak Base Vessel

- 0.63/04699 rev 01 and 02 Weak Base Bottom Collector Lateral Details

- 0.63/01852.02 General Arrangement of Strong Base Vessel

- 0.63/4701 rev 01 and 02 Regenerant Collector Strong Base

- 0.63/4703.001 Strong Base Bottom Distributor

- 0.63/01853.02 General Arrangement of Mixed Bed Vessel

- 0.63/4709.01 Bottom Regenerant Distributor Mixed Bed

- 0.63/4711.01 Top Regenerant Distributor Lateral Details Mixed Bed

- 0.63/4707 rev 03 Regenerant Collector Mixed Bed

- 0.63/1854 rev 02 Resin Separation and Cation Regeneration Units

- 0.63/1855 rev 02 Anion Regeneration Units General Arrangement

- 0.63/1856 rev 02 Resin Storage Units General Arrangement

| SCOPE OF WORK - Pre-Inspection for scope quantification including spark test. - Stripping out of old rubber in the vessel where required as identified and marked out during inspection. - Removal and reinstallation of laterals where required to execute scope and to do repairs where identified. - Removal and reinstallation of headers where required. Plastic welding of header if cracks are found during inspection. - Surface preparation (blasting, grinding) and Rubber lining of the vessel, manhole covers, nozzles, brackets and supports where needed. - Extraction of blasting material to outside of water treatment building. - Use of stainless steel bolts, nuts and washers. - Removal and casting of vessel floor where required or a Tekapor floor ring repair if deemed suitable option. - Repairs/replacement of broken and/or damaged laterals. - Wrapping of the laterals. - Rubber testing required during pre-inspection and post-inspection and to include : - Final Spark test - Final Hardness test - Post Inspection including housekeeping and cleanliness of vessel. - Certification and report of work completed. - Removal, cleaning and reinstallation of sight glasses. - Disposal of waste at designated area. - Provide Data pack including QCP, method statement, testing certificates, material certification, NDT report and inspection report. - The contractor must have a CIDB grading CE5 and ME5 PS: the actual bill of quantities can only be quantified after a full inspection has been done. Possible exclusion on some of the works is to be expected and additional work may also be required. | SCOPE OF WORK EXCLUSIONS: - Application for train vessels Permit to work (PTW). - Cation vessel - Weak Base vessel - Strong base vessel - Mixed vessel bed - CPR Cation - CPR Anion - Permit to Work will be issued by Eskom and responsibility handed over to the Contractor’s Appointed Supervisor. - Application for gas test to enter vessel. - Eskom to remove and de-load resin and rinse vessel. - Opening of vessel manholes and removal of bottom vessels elbows. - Building of scaffolding. - Cleaning and flushing of laterals. - Loading of resins. - Any weld repairs identified. |
| --- | --- |

GENERAL INFORMATION

Demin train operation conditions - Operating Temperature: Ambient - Operating Pressure: 0-650kPA - Flow range: 0-250m3/hr (220 design) Demin Train Regeneration conditions - Regenerating temperature: Max 45oC - Caustic strength (NaOH): 5% - Weak Base, Strong Base and Mixed Bed vessel - Acid strength (H2SO4): 5% - Cation vessel and Mixed Bed Vessel CPR Vessel Regeneration conditions - Regenerating temperature: Max 40◦C - Acid strength (H2S04): 6% - Cation CPR - Caustic strength (NaOH): 6% - Anion CPR - Medium: Demin water - Design pressure: 785 kPa(a) Other Table 1: Vessel and Resin information Vessel Name; Size (Dia, T/T Dim); Vessel Functional Location; Type; Resin Type. Cation Exchange Vessel; 3000 X 4800; 10UB31G001; Strong Cation 1; Amberjet 1300 H. Weak Cation 1; Amberlite IRC86SB. 10UB32G001; Strong Cation 2; Amberjet 1500 H. Weak Cation 2; Amberlite IRC86SB. 10UB33G001; Strong Cation 3; Amberjet 1500 H. Weak Cation 3; Amberlite IRC86SB. Anion Weak Base Exchange Vessel; 3000 X 2400; 10UB31G001; Weak Anion 1; Amberlite IRA96. 10UB32G001; Weak Anion 2; Amberlite IRA96. 10UB33G001; Weak Anion 3; Amberlite IRA96. Strong Base Exchange Vessel; 2800 X 3000; 10UB41G001; Strong Anion 1; Dowex Marathon A. 10UB42G001; Strong Anion 2; Amberjet 4200 Cl. 10UB43G001; Strong Anion 3; Amberjet 4200 Cl. Mixed Bed Exchange Vessel; 2400 X 2250; 10UB51G001; Strong Cation MB 1; Amberjet 1600 H. Strong anion MB 1; Amberjet 9000OH. 10UB52G002; Strong Cation MB 2; Amberjet 1600 H. Strong anion MB 2; Amberjet 9000OH. 10UB53G003; Strong Cation MB 3; Amberjet 1600 H. Strong anion MB 3; Amberjet 9000OH. Cation/Separation CPR Vessel; 2000 X 3400; 10UC11/21/31G001; Cation; Amberjet 1600H. Anion CPR Vessel; 1500 X 3200; 10UC12/22/32G001; Anion; Amberjet 9000 OH. CPR Storage Vessel; 2000 X 2850; 10UC13/23/33G001; N/A; N/A.

CONTRACTOR SHALL PROVIDE/SUPPLY:

- The QCP plan, method statement and the project implementation programme to be provided by the Contractor before work starts. - Product data sheet for the rubber, adhesives and the floor to be used with relevant specifications (tensile strength, elasticity, SG etc., type grade, class.) - Contractor to make provision for test samples. A test sample of test plate at area of work to be provided. - Contractor shall provide adequate lighting for inspections and during actual work activities inside vessel. - The batch certificates of rubber and other products used will form part of the data pack. - It is the responsibility of the contractor to ensure that the safety measures are adhered to in terms of the OSH act. The vessel is classified as confined space as per OHS Act Referenced above. The portable electrical tools need to comply with section 10 of the electrical installation regulations and the portable lights to section 11(2). - All necessary Safety equipment, air supply and extraction fans to be supplied by contractor. Refer to Section for Preparation Work Required by Contractor for more detail. - The Contractor shall supply a detailed report on the material and specifications used for the project. - All measurements to be confirmed on site and laterals to be supplied and manufactured as per samples and technical specifications of drawings. - Project team members to include a project supervisor, skilled individuals to carry out rubber lining and tekapor floor replacement with 2 years relevant experience. Notes: - Carbon bisulphites not allowed within Eskom’s premises. - Where glue-ing of connection may be required. No silica compound may be used. - Plastic welding where needed shall be done after the procedure has been accepted by Eskom. Welding procedure is to be submitted by the Contractor. All welding documentation will be subject to approval by the AIA (Approved Inspection Authority). The main contractor or subcontractor to provide proof of qualified thermoplastic welder compliant to SANS 10269. Plastic welds to SANS 10270. Quantities on the scope are only estimates. Final quantities will be done after the pre-inspection. To be as per sample.

PREPARATION WORK REQUIRED BY CONTRACTOR

- Contractor to establish site, move all required equipment to site and to provide all experienced labourers with all materials required to carry out the scope. - Provide trained Appointed Supervisor to supervise the work. - Housekeeping and site clearance. The area to be kept clean and vessel to be clean after work has been carried out. - Disposal of failed tekapor base into skips provided outside Water Treatment Plant Building. - The Contractor shall provide all supervision, labour, materials, consumables, equipment, tools and incidentals required to carry out the Works. - All Works have to be performed in accordance with the accepted and signed Quality Control Plan and Method Statement. - The Contractor will provide electrical supply that is required and to provide necessary white lights for inspection. - The Contractor should provide compressed air (dry). - All materials to be ready for installation for when a plant section is taken out. Subject to plant availability. - A compulsory kick-off meeting to be held before work commences with Contractor and all relevant stakeholders. - The Contractor is required to submit daily feedback to the Project Manager to discuss areas of concern, hold-ups and progress due to production risk. - The Contractor is responsible for disposal of abrasive/spent grit and for final site clearance. - It will be the Contractor’s responsibility to handle, load, transport and unloading of all materials from Contractor’s designated area of issue to work site of client. - The area for site establishment will be indicated before work can start by Employer. - Contractor is responsible for electrical supply connection. - Provide certified lifting equipment and qualified rigger/s if required. - Contractor is responsible for providing required crane, lifting equipment, scaffolding, and rigging supplies to execute scope of Works. - Set up rigging equipment to remove and install required equipment. - Personal safety wear for plant area and conditions is to be provided by the Contractor for all site personnel and to be utilized at all times. - It will be the responsibility of the Contractor to contain/extract dust during abrasive blast activities inside the Water Treatment Plant Building. - The Contractor to provide all extraction equipment for blasting activities required inside the building. Dust must be routed to the outside of the water treatment building. The Contractor must provide all ventilation equipment where required to comply with relevant standards. - The Contractor is responsible for site-destablishment and site clearance.

SCOPE OF WORK DETAILED BREAKDOWN

- PRE-INSPECTION FOR ALL VESSELS

| DESCRIPTION OF WORK | SPECIFICATION | REMARKS | RESPONSIBLE PERSON |
| --- | --- | --- | --- |
| - PRE-INSPECTION |  |  |  |
| Rubber integrity in all vessels, support beams, manhole and nozzles. | Spark test, hardness test and visual damages | Mark all damaged areas. | Contractor Eskom to be present during inspection. |
| Floor integrity in vessel | Air test Draining test Loose grid Hammer test Cracks and gaps around circumference of floor | Determine full base re-cast or only ring repair. | Contractor Eskom to be present during inspection. |
| Inspection on all laterals and inspection for cracked/bent headers | Visual damages | Removal and replace damaged laterals and repair damaged headers. | Contractor Eskom to be present during inspection. |
| Shell thickness after rubber has been stripped in all vessels. | Wall thickness and visual damages |  | Contractor Eskom to be present during inspection. |
| Inspection of all welds where rubber was stripped and surface blasted. | Visual damages | Only when required. | Contractor Eskom and AIA to be present during inspection. |
| Inspection of CPR Vessel bottom mesh screen and headers. | Visual damages | Removal and replace damaged components with provided spares. | Contractor Eskom to be present during inspection. |

- CATION VESSELS

| DESCRIPTION OF WORK | SPECIFICATION | REMARKS | RESPONSIBLE PERSON |
| --- | --- | --- | --- |
| - CATION VESSELS |  |  |  |
| Rubber Lining |  |  |  |
| Vessel internal shell: Rubber stripping Grinding rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 10m2 Mid Shell: 46m2 Bottom dish: 10m2 Vessel dimension: 3000 mm x 4800 mm | Covering of all inlet/outlet water and resin pipes. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) | Contractor |
| Vessel internal beams and brackets | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:10m2 (Aprox.) | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP. | Contractor |
| Nozzle on bottom dish | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Size: 80 NB Length: 1000 mm Overlapping of flange face. | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP. | Contractor |

| VESSEL FLOOR BASE |  |  |  |
| --- | --- | --- | --- |
| Floor Replacement | Tekapor/Sinert base porous floor The flow requirement for the vessel throughput on the new floor shall be 220m3/h. Volume approx 1.0m3 Compaction to be uniform during casting. Resin sizes to be verified on site. Contractor to provide size distribution for 6 layers of stones required in vessel as per samples. | Tekapor floor - Floor material must be porous and resistant to acid attack on the cation vessel and caustic attack on the anion vessels, also preventing resin to drain via the floor (well bonded to the side vessel wall). Particle size distribution certificate to be provided for sand. Level of dryness and cleanliness to be confirmed. The sand epoxy mixture to be homogenous no clumping prior to casting. QCP to include the mixing time, casting time, compaction time and time in which next layer should be casted. Hold point to inspect mixture for clumps before casting. Including damaged base removal. | Contractor |
| Rubber Lining on shell only: Rubber stripping Grinding Rubber lining Sandblasting before application of rubber if dome is stripped based on inspection after Tekapor/Sinert base porous floor is removed. | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:10m2 | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP. | Contractor |
| Under floor laterals | As per sample Shape: Spiral solar system shape Orbits: Nine orbits per side Material: PVC Bottom HDPE lateral with top plate Vessel Diameter: 3m | Drawings can be provided upon request. | Contractor |
| Laterals All measurements to be verified on site and manufactured according to sample. |  |  |  |
| Effluent Laterals | Bottom green cloth wound laterals Quantities: 22 Diameter: 50mm Material: PVC drilled 10mm NB holes spaced 100mm apart. As per sample. | Heat-shrink to be applied on the ends of the laterals. Drawings can be provided upon request. | Contractor |
| Injection laterals | Bottom green cloth wound laterals Quantities: 18 Diameter: 10mm Material: Fine grid stainless steel and plastic covered PVC drilled 10mm NB holes spaced 100mm apart. As per sample. | Heat-shrink to be applied on the cloth wound laterals end. Drawings can be provided upon request. | Contractor |
| Header | As per sample. | To be plastic welded if repair required. | Contractor |

- WEAK BASE VESSELS

| DESCRIPTION OF WORK | SPECIFICATION | REMARKS | RESPONSIBLE PERSON |
| --- | --- | --- | --- |
| - WEAK BASE VESSELS |  |  |  |
| Rubber Lining |  |  |  |
| Vessel internal shell: Rubber stripping Grinding, Sand blasting, Cleaning, Rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 10m2 Mid Shell: 23m2 Bottom dish: 10m2 Vessel dimension: 3000 mm x 2400 mm | Covering of all inlet/outlet water and resin pipes Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) Rubber lining on bottom dish will be done if the floor is to be replaced. | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Vessel internal beams, brackets and joints. Rubber stripping Grinding, Sand blasting, Cleaning, Rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:10m2 | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) | Contractor Surface profile and cleanliness – Hold Point for Eskom. |

| VESSEL FLOOR BASE: |  |  |  |
| --- | --- | --- | --- |
| Floor Replacement | Tekapor/Sinert base porous floor The flow requirement for the vessel throughput on the new floor shall be 220m3/h. Volume approx 1.0m3 Compaction to be uniform during casting. Resin sizes to be verified on site. Contractor to provide size distribution for 6 layers of stones required in vessel. Sample Test block to be supplied for the floor that is to be replaced. | Tekapor floor - Floor material must be porous and resistant to acid attack on the cation vessel and caustic attack on the anion vessels, also preventing resin to drain via the floor (well bonded to the side vessel wall). Casting to be continuous. Particle size distribution certificate to be provided for sand. Level of dryness and cleanliness to be confirmed. The sand epoxy mixture to be homogenous no clumping prior to casting. QCP to include the mixing time, casting time, compaction time, time in which next layer should be casted, curing time, and record weather conditions. Hold point to inspect mixture for clumps before casting, wall clearance after casting. QCP to include acceptance criteria. Including damaged base removal. | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Rubber Lining on shell only: Rubber stripping Grinding rubber lining Sandblasting before application of rubber if dome is stripped based on inspection after Tekapor/Sinert base porous floor is removed. | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:10m2 | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Under floor laterals | As per sample Shape: Spiral solar system shape Orbits: Nine orbits per side Material: PVC Bottom HDPE lateral with top plate Vessel Diameter: 3m | Drawings can be provided upon request. | Contractor |
| Laterals All measurements to be verified on site and manufactured according to sample. |  |  |  |
| Effluent Laterals | As per sample. Bottom green cloth wound laterals Quantities: 22 Diameter: 10mm Material: Fine grid stainless steel covered PVC, drilled to 10mm NB holes spaced 100mm apart. | Heat shrink to be applied on the ends of the laterals. Drawings can be provided upon request. | Contractor |
| Header | As per sample. | To be plastic welded if required. | Contractor |

- STRONG BASE VESSELS

| DESCRIPTION OF WORK | SPECIFICATION | REMARKS | RESPONSIBLE PERSON |
| --- | --- | --- | --- |
| - STRONG BASE VESSELS |  |  |  |
| Rubber Lining |  |  |  |
| Vessel internal shell: Rubber stripping Grinding, Sand blasting, Cleaning, Rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 9m2 Mid Shell: 29m2 Bottom dish: 9m2 Vessel dimension: 2800 mm x 3000 mm | Covering of all inlet/outlet water and resin pipes Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) Rubber lining on bottom dish will be done if the floor is to be replaced. | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Vessel internal beams, brackets and joints. Rubber stripping Grinding, Sand blasting, Cleaning, Rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:10m2 | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) | Contractor Surface profile and cleanliness – Hold Point for Eskom. |

| VESSEL FLOOR BASE: |  |  |  |
| --- | --- | --- | --- |
| Floor Replacement | Tekapor/Sinert base porous floor The flow requirement for the vessel throughput on the new floor shall be 220m3/h. Volume approx 1.0m3 Compaction to be uniform during casting. Resin sizes to be verified on site. Contractor to provide size distribution for 6 layers of stones required in vessel. Sample Test block to be supplied for the floor that is to be replaced. | Tekapor floor - Floor material must be porous and resistant to acid attack on the cation vessels and caustic attack on the anion vessels, also preventing resin to drain via the floor (well bonded to the side vessel wall). Casting to be continuous. Particle size distribution certificate to be provided for sand. Level of dryness and cleanliness to be confirmed. The sand epoxy mixture to be homogenous no clumping prior to casting. QCP to include the mixing time, casting time, compaction time, time in which next layer should be casted, curing time, and record weather conditions. Hold point to inspect mixture for clumps before casting, wall clearance after casting. QCP to include acceptance criteria. Including damaged base removal. | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Rubber Lining on shell only: Rubber stripping Grinding rubber lining Sandblasting before application of rubber if dome is stripped based on inspection after Tekapor/Sinert base porous floor is removed. | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:9m2 | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Laterals All measurements to be verified on site and manufactured according to sample. |  |  |  |
| Floor Bottom Laterals | As per sample. Shape: Spiral solar system shape Orbits: Nine orbits per side Material: PVC Bottom HDPE lateral with top plate | Drawings can be provided upon request. | Contractor |
| Laterals |  |  |  |
| Effluent Laterals | Bottom green cloth wound laterals Quantities: 16 Diameter: 50mm Material: PVC drilled 10mm NB holes spaced 100mm apart. | Heat shrink to be applied on the ends of the laterals | Contractor |

- MIXED BASE VESSELS

| DESCRIPTION OF WORK | SPECIFICATION | REMARKS | RESPONSIBLE PERSON |
| --- | --- | --- | --- |
| - MIXED BED VESSELS |  |  |  |
| Removal of laterals and headers |  | Laterals and headers will be clearly marked for correct re-installation purposes. | Contractor |
| Repairs of headers |  | Plastic welding of header shall be done after the procedure has been accepted by Eskom | Contractor |
| Supply of header O-rings for the sealing to T-pieces to the header | Diameter : 50mm Quantity : 100 | No silica based compound on the O-rings. | Contractor |
| Floor nozzles replacement | See attached image in Appendix A. Quantity: 10 | As per sample. | Contractor |
| Laterals | Bottom green cloth wound laterals Quantities: 10 Diameter: 50mm Material: PVC drilled 4mm NB holes spaced 100mm apart. |  | Contractor |

| Rubber Lining |  |  |  |
| --- | --- | --- | --- |
| Vessel internal shell: Rubber stripping Grinding, Sand blasting, Cleaning, Rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 7m2 Mid Shell: 22m2 Bottom dish: 7m2 Vessel dimension: 2400 mm x 2250 mm PLEASE NOTE “GAM MAT 21 62” does not explicitly mention mixed bed in the template table but all parameters contained in the vessel are suitable for the rubber lining specification and information as per this specification. | Covering of all inlet/outlet water and resin pipes Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) Rubber lining on bottom dish will be done if the floor is to be replaced. | Contractor Surface profile and cleanliness – Hold Point for Eskom. |
| Vessel internal beams, brackets and joints. Rubber stripping Grinding, Sand blasting, Cleaning, Rubber lining | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity:10m2 | Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) | Contractor Surface profile and cleanliness – Hold Point for Eskom. |

- CPR CATION VESSELS

| DESCRIPTION OF WORK |  | SPECIFICATION |  | REMARKS |  | RESPONSIBLE PERSON |
| --- | --- | --- | --- | --- | --- | --- |
| CPR Cation Vessels |  |  |  |  |  |  |
| Rubber Lining |  |  |  |  |  |  |
| - Rubber Lining of shell: - Rubber stripping, Grinding, blasting, rubber lining of shell. - Rubber Lining of nozzle and flange surfaces: - Rubber stripping, Grinding, blasting, rubber lining Sandblasting before application of rubber if once stripped. | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 5m2 Mid Shell: 22m2 Bottom dish: 5m2 Other: 10m2 (includes rubber lining on nozzle, flange surfaces, manway) Vessel dimension: 2000 mm x 3400 mm PLEASE NOTE: even though not specifically mentioned in “GAM MAT 21 62” the rubber lining specification and method of application is sufficient for these vessels. |  | Refer to Drawing 063/1854 rev 02 Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) |  | Contractor |  |

- CPR ANION VESSELS

| DESCRIPTION OF WORK |  | SPECIFICATION | REMARKS |  | RESPONSIBLE PERSON |  |
| --- | --- | --- | --- | --- | --- | --- |
| CPR Anion Vessels |  |  |  |  |  |  |
| Rubber Lining |  |  |  |  |  |  |
| - Rubber Lining of shell: - Rubber stripping, Grinding, blasting, rubber lining of shell. - Rubber Lining of nozzle and flange surfaces: - Rubber stripping, Grinding, blasting, rubber lining Sandblasting before application of rubber, once stripped. | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 3m2 Mid Shell: 15m2 Bottom dish: 3m2 Other: 10m2 (includes rubber lining on nozzle, flange surfaces, manway) Vessel dimension: 1500 mm x 3200 mm PLEASE NOTE: even though not specifically mentioned in “GAM MAT 21 62” the rubber lining specification and method of application is sufficient for these vessels |  |  | Refer to Drawing 063/1855 rev 02 Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) |  | Contractor |

- CPR Storage VESSELS

| DESCRIPTION OF WORK |  | SPECIFICATION | REMARKS |  | RESPONSIBLE PERSON |  |
| --- | --- | --- | --- | --- | --- | --- |
| CPR Anion Vessels |  |  |  |  |  |  |
| Rubber Lining |  |  |  |  |  |  |
| - Rubber Lining of shell: - Rubber stripping, Grinding, blasting, rubber lining of shell. - Rubber Lining of nozzle and flange surfaces: - Rubber stripping, Grinding, blasting, rubber lining Sandblasting before application of rubber, once stripped. | Internal lining: In accordance with GAM MAT 21 62 in conjunction with 240-101712128. Quantity: Top dish: 5m2 Mid Shell: 18m2 Bottom dish: 5m2 Other: 10m2 (includes rubber lining on nozzle, flange surfaces, manway) Vessel dimension: 2000 mm x 2850 mm PLEASE NOTE: even though not specifically mentioned in “GAM MAT 21 62” the rubber lining specification and method of application is sufficient for these vessels |  |  | Refer to Drawing 063/1856 rev 02 Vessel to be cleaned after sand blasting before rubber lining. Cleanliness before rubber lining to form part of the QCP and vessel to be cleaned. (Blast material – Low Silica Content) |  | Contractor |

F) POST INSPECTION AND ACCEPTANCE CRITERIA FOR ALL VESSELS

| DESCRIPTION OF WORK | SPECIFICATION | REMARKS | RESPONSIBLE PERSON |
| --- | --- | --- | --- |
| - POST INSPECTION AND ACCEPTANCE CRITERIA |  |  |  |
| Rubber inspection | Hardness test Spark Testing Visual Inspection Material certificate Vessel cleanliness. | Hardness test shall conform to specification as per rubber type. Calibration information on spark test and hardness test measurement to be provided before inspection for approval. | Eskom and Contractor |
| Floor inspection | Floor tests shall include: - Air leak test, - Drain effluent - Fine loose grid - Rubber Hammer test to inspect for hollowness of casted base. - Inspect for cracks around circumference of floor. - Perform a scrapper/steel wire brush test on the surface of the base to test for fine loose grid. - Apply a 0.3 mm feeler gauge around the circumference of the base to ensure there are no gaps. | Two completed reports including specifications or MSDS of materials used, tests reports as per vessel completed. Sample of casting to remain property of Lethabo Power Station. | Contractor (Eskom to Witness inspection) |
| Certification and report of works completed | Rubber certification in term of SANS1198 |  | Contractor |
| Testing and cold commissioning | Expected flow throughout - 220m3/hr Flow variations of not more than 10% of the throughput after a minimum of 5 regenerations from commissioning date |  | Eskom, Contractor to witness initial commissioning |

RUBBER LINING REQUIREMENTS

Rubber lining and coating according to: • GAM MAT 21 62 Lethabo IX and WTP Vessels Patch and Relining 24 May 2021 To be read in conjunction with 240-101712128: “Standards for the Internal Corrosion Protection of Water Systems, Chemical Tanks and Vessels and Associated Piping with Linings”

Quality Control and Assurance

Rubber lining and coating specifications according to: - GAM MAT 21 62 Lethabo IX and WTP Vessels Patch and Relining 24 May 2021 Other specific requirements: - The Contractor must produce and submit a quality control plan (QCP) and submit to the Employer for approval before work is started. - The QCP must comply with Employer’s GGS0465 revision 1 standard, point number 4.5 (QCP requirements). - The quality plan must indicate relevant hold and witness points to be agreed upon by the Employer and must be according to scope requirements. - The Contractor must submit a copy of his/her quality policy manual and quality system procedures relevant to the scope of the enquiry. - If the Contractor is ISO 9001:2000 accredited, a copy of the certificate must be submitted. - The Contractor must submit his/her typical quality control plan with tender returnables. - The successful Contractor must submit all the quality management documents listed in Employer’s GGS0465 revision 1 standard, point number 4.3.1 prior to the start of the contract. - The contractor must supply a data pack in the format of a soft and hard copy. The data pack to include method statements, QCPs, etc. The Contractor conforms to the following Quality Management requirements: - The quality requirements are as per ISO 9001 and Eskom Standard Quality Requirements for Engineering and Construction work (refer to forms QA001/A and QA001/ B for the applicable sections). - Documents submitted for review and acceptance by the Project Manager after the Contract Date and prior to the commencement of work. - The Contractor submits a fully detailed Quality Management Programme (QAP) for acceptance within four weeks of the Contract Date. - No work is allowed on Site unless the Employer accepts the QAP, QCP and Method Statement. - The Contractor utilises the Employer’s quality documentation forms for requesting access, erection checks etc. These request forms is to be submitted to the Supervisor at least one week prior to the requested activity, or as agreed to by the Project Manager. The Contractor submits a quality report on a monthly basis, including the following: - A list of Defects with those older than 30 days being flagged and an explanation attached - Monthly updated Site and pre-site programmes - Foreign inspection dates - Inspections completed/outstanding - Register of accepted Defects - Project Quality progress report The Contractor submits the following: - QA plan/manual - I&TP's - Organogrammes (changes only with the Project Manager's acceptance) - Copy of all work instructions and procedures when requested by the Project Manager.

Safety, Health and Environmental (SHE) Requirements

- The Contractor must comply with Employer’s Construction SHE management procedure (32-136). - The Contractor must submit the SHE file that will be audited and accepted by the Employer two weeks before works commence. - The Contractor will have to have all staff go through induction training the week before work starts.

Hazardous Waste Disposal and Handling (Contractors responsibility) - Hazardous / toxic waste includes all waste which contains elements or compounds listed as hazardous substances in terms of the Hazardous Substances Act No. 15 of 1973. - Any Contractor who produces hazardous waste on site will be responsible for the safe removal of such waste to a registered Class I site by a waste removal and disposal body. - All disposal of waste to be in accordance with LBE22004PC Lethabo Waste Management Procedure and the on-site Environmental Department consulted where required; - According to of the Environmental Management Waste act 59 0f 2008: GNR 634: Waste Classification and Management Regulation; and GNR 635 National Norms and Standards for Assessment of Waste for Disposal of waste to Landfill Site, All generators of waste is required to classify and assess waste streams generated. - The Contractor is responsible for disposal of abrasive/spent grit used on site as per procedure. - Spent abrasive blasting grit was classified as hazardous Type 2 waste. This means it should be disposed at any licensed Class A landfill facility (H:H), thus it is necessary to dispose it a hazardous landfill such as Holfontein landfill site. - Provide canvas sheets for soil protection to store grit blasting material or resin if required. - It will be the Contractor’s responsibility to remove, load, transport and dispose of old equipment to the Lethabo Salvage Yard. - Disposal of waste to be in accordance with Section 4 and LBE 22004PC Lethabo Waste Management Procedure and the on-site Environmental Department consulted where required. Lighting and Electrical Supply - The Contractor shall supply and install lighting as required facilitating contract execution and ensure adequate lighting is available for Quality inspections. - Furthermore, intrinsic safe electrical equipment may be used only. - All electrical equipment used has to have a valid certificate of compliance (COC). - The vessels on the Water Treatment Building, covered in this scope, at Lethabo Power Station are classified as ‘Confined space’. - The portable electrical tools need to comply with section 10 of the electrical installation regulations and the portable electrical lights to section 11 (2) deals specifically with confined spaces. Lights that exceed 50V the earth leakage protection be earthed to the vessel to prevent electrocution in the case of accidental discharge. The standard referred to is SANS767-1. - Any portable electrical tools need to comply to section 10 of the OHS Act Electrical Machinery Regulations: - No person shall use or permit the use of a portable electric tool with an operating voltage that exceeds 50 V to earth unless- - it is connected to a source of electrical energy incorporating an earth leakage protection device, the construction of which meets the requirements of the relevant health and safety standard incorporated into these Regulations under section 44 of the Act; or - it is connected to a source of electrical energy through the interposition between each tool and the source of an individually double-wound isolating transformer, the secondary winding of which is not earthed at any point and the construction of which meets the requirements of the relevant health and safety standard incorporated into these Regulations under section 44 of the Act; or - it is connected to a source of high frequency electrical energy derived from a generator which is used solely for supplying energy to such portable electric tool and which arrangement is approved by the chief inspector; or - it is clearly marked that it is constructed with double or reinforced insulation. - No person shall sell a portable electric tool constructed with double or reinforced insulation referred to in sub regulation (1) (d) unless- - it is clearly marked that it is constructed with such insulation; and - its insulation is constructed in accordance with the relevant health and safety standard incorporated into these Regulations under section 44 of the Act. - No Employer or user shall use or permit the use of a portable electric tool which is not fitted with a switch to allow for easy and safe starting and stopping of the tool. - The Employer or user shall maintain every portable electric tool, together with its flexible cord and plug, in good working order. GENERAL REQUIREMENTS OF SCOPE OF WORKS TO BE CARRIED OUT - The Contractor is required to carry out the Works as specified. - Before the work can start on site the Contractor must provide all relevant and required documentation as stipulated in the scope of work and referenced standards for approval by the Employer. - Once all required documentation (QCPs, Method Statement, Project Programme, Datasheets) have been approved by the Employer the Contractor to mobilize to site as per instruction from the Employer. - Site establishment/mobilization to consider inclement weather conditions e.g. storage of equipment, suitable electrical supply cables and distribution boards for inclement weather conditions. - The Contractor is responsible for good housekeeping at all times and the Employer reserves the right to raise housekeeping issues for the Contractor to address. - Any damage caused by the Contractor to any portion of plant not intended to be worked on, shall be repaired by the Contractor, at the Contractor’s expense, to the satisfaction of the Employer. - Any equipment, instrumentation, auxiliaries, electrical supplies that are damaged in any way by construction operations; it shall be repaired or replaced by the Contractor at his own expense. - Supply, transport and deliver all equipment, spares, supplies, tools remains the responsibility of the Contractor. - All equipment, consumables and materials delivered to site to be approved by the Employer. - All equipment, consumables and materials delivered to be suitable for the plant application. - Material Certificates, Specification data sheets and all relevant documentation to be provided upon delivery of equipment and materials for approval by the Employer. - Any consumables required for installation and operation of equipment must be provided by Contractor. - All measurements to be verified on site by the Contractor and verified against drawings. - All lining systems to comply with the Eskom Corrosion protection standard: 240-101712128 Standard for the Internal Corrosion Protection of Water Systems, Chemical Tanks and Vessels and Associated Piping with Linings. - The Contractor is responsible for quality control and should provide all the equipment necessary to do so. The required equipment for coating and linings are stipulated in the 240-101712128 Eskom Corrosion protection standard. - Recycling of spent abrasive grit is not permitted. - Contractor to provide all required testing equipment and inspection lights for inspection activities by Employer and AIA. - The Contractor to submit a detailed method statement and all product data sheets for equipment/lining/coating for approval by Employer before work can start. - If at any stage of this contract it is found that the Contractor has deviated from the requirements of this specification, whether it be by the installation of equipment not specified, etc. or otherwise, without prior WRITTEN consent from the Employer, the Employer shall have the right to order the Contractor to remove such items, etc. constituting the deviation and replace it with the exact item, etc. specified, without any adjustment in the tender price. - All work shall be quality work, performed according to the standards of the industry and to the complete satisfaction of the Employer. Any discrepancies or previously unknown field conditions shall be brought to the attention of the Employer and resolved before continuing the work. - If any equipment or material to be used complies with a standard issued by a recognised international standards organisation, then such compliance should be stated in the tender documents (Price Schedule). - All equipment or material to be used in this installation shall be new and of an acceptable quality to the Employer. - All consumables (e.g. bolts, nuts, washers, U-bolts etc.) required, must be supplied by the Contractor. It is the Contractor’s responsibility to ensure the materials are compatible with the system. - Relevant information and details shall be submitted to the Employer for approval. - All Works have to be performed in accordance with the accepted and signed Quality Control Plans. - The responsibility and the decision-making powers regarding the operation of the Equipment shall remain with the Employer. - The Contractor is not allowed to sub-contract any work which was not disclosed at the time of the tender without the written permission of the Employer. The quality of sub-contracted work will remain the responsibility of the Contractor. - The repairs shall be carried out on an as and when required basis. - The Contractor shall provide all supervision, labour, materials, consumables, equipment, tools and incidentals required to carry out repairs of vessels. Proof of calibration for testing equipment to be provided. - The lead time for spares and duration of work to be executed to be determined after vessel inspection. - The Contractor shall comply with the listed standards. - Any rework will be at the expense of the Contractor (this include all cost). Commissioning, test, verify performance and hand-over. - Clear PTW and monitor equipment for 30 days. - Contractor to Compile defect list as indicated by Lethabo PS and resolve/correct any issues. - Sign final acceptance after a successful full production run and regeneration test run if there are no defects after all defects/technical issues have been rectified in point above. - Hand-over to Lethabo PS and Final Sign off of all Data Packs. Data Packages - Data Packs to be provided by the Contractor to the Employer for Final sign off. - The Contractor to submit a hard copy, 1 soft copy in PDF format and 1 native updatable copy for all data packs to the Employer. - Contractor’s scope of work includes but is not limited to providing the following documentation as part of the data packages: - Copies of all inspections, test reports and photographs (with date and time) - Non-conformance reports. - Cleanliness clearance certificate. - Generic reports on all other findings and corrective measures used. - Completed and signed off QCP’s. - Welding Procedure - Thermoplastic Welder Qualifications - Inspectors qualified to SAQCC (Corrosion Protection) ‘Coating Inspectors’ Level 1 (shop inspections) or Level 2 (site inspections) or NACE Coating Inspection Programme (CIP). - Copies of all approved procedures and method statements. - Test and Calibration Certificates. - Batch Certificates for all products. - Sample test blocks with pull test results. - Blasting profile inspection report and acceptance. - Material Certificates and Specification and Material data sheets. - Organogram specific reference to be made to personnel performing QC and supervisors. - Project programme. Constraints - The scope of work is uncertain since the extent and type of some damages cannot be defined before internal inspection. The Contractor shall provide the possible solutions up front with their prices in rates. - The Contractor shall adhere to the clearly defined project milestones and project management principles to avoid delays. - Work must be done according to the technical specification provided. - The Contractor is not allowed to do anything other than what has been stipulated in the contract, drawings, approved method statement, and quality control plans, unless instructed to do so by the Employer’s representative in writing. - Plant where scope will be executed: West Water Treatment Plant – indoors. Transportation and Storage - Transport and storage shall conform to the following requirements: - On delivery the equipment shall be dry externally and internally and ready for installation. - Every precaution shall be taken to prevent damage to all equipment and materials during transportation and delivery to site. Under no condition will damaged equipment be accepted by the Employer. - Equipment and materials must be stored in a manner which will assure the protection of the materials and equipment from damage, theft and to keep it clean. - All required materials to comply with storage requirements as per Safety Data Sheet. - Designated storage area to be identified by Employer before work will commence.

  - Constraints on how the Contractor Provides the Works

Task Order process (Option A2 only)

The Employers’ Representative, or his delegate, issues a unique Task Order for Non Destructive testing services required.

Intentions of the Employer before Completion

- The Employer reserves the right to carry out any checks, on quantities and categories of the personnel supplied per Task Order.

- The Employer reserves the right to carry out any checks, or conduct any physical inspections or tests, on the service provided.

Requirements for the program

- The contractor must develop a detailed program that indicate what will be done from start to finish.

- Should the programme change during the execution of the work, the Contractor must supply the Employer with an updated programme indicating the change in the programme and the effect it would have on the completion of subsequent activities.

- The Contractor must supply a Process Quality Plan of the work activities to the Employer one day after the order award date, for approval and inclusion of inspection points to be witnessed by the Employer’s Representative.  Work may only continue once the Process Quality Plan has been approved by the Employer.

- The Contractor will inform the Employer three days in advance of reaching an inspection hold point.

- Work may not continue beyond any point on the Process Quality Plan, marked as a Hold Point by the Employer, if the Hold Point has not been signed off on the Process Quality Plan by the Employer’s Representative.

## 1.3 Interpretation and terminology

The following abbreviations are used in this Service Information:

| Abbreviation | Meaning given to the abbreviation |
| --- | --- |
| Contractor: | Service provider contracted for supplying specific service to Eskom, Lethabo Power Station. |
| Employer: | Eskom, or Eskom Lethabo Power Station |
| BS: | British Standard |
| BU: | Business Unit |
| EMS: | Environmental Management System |
| ISO: | International Standards Organisation |
| KKS: | Kraftwerk Kennzeichen System |
| LPG: | Liquid Petroleum Gas |
| NEC: | New Engineering Contract |
| NPSH: | Net Positive Suction Head |
| ORHVS | Operating Regulations for High Voltage Systems |
| PCLF: | Planned Capability Loss Factor |
| PM: | Plant Maintenance |
| PSR | Plant Safety Regulations |
| PTW: | Permit to Work |
| QA: | Quality Assurance |
| QC: | Quality Control |
| QCP: | Quality Control Plan |
| QMP: | Quality Management Programme |
| SABS: | South African Bureau of Standards |
| SANS: | South African National Standards |
| SAP PM: | SAP Plant Maintenance |
| SAP: | Systems, Applications, Products (Plant Maintenance, Procurement, Finance and Materials Management) integrated maintenance management system. |
| SOW: | Scope of Work |
| STEP: | Station Thermal Efficiency Program |
| UCF: | Unit Capability Factor |
| UCLF: | Unplanned Capability Loss Factor |

- 2 Management strategy and start up

- 2.1 The Contractor’s plan for the service

- To be discussed before any task can be carried out between the Contractor and Employer.

- Programme to be supplied on request on a signed hard copy as well as a soft copy, see Scope of Work.

- No work shall commence until the scope of work has been finalised and accepted by both the          Service Manager and Contractor.

- Contractor and Service Manager will do a final inspection on the completion of the scope of work before signing of any documents

- 2.2 Management meetings

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.

Attendance of meetings as required by Service Manager such as:

-	Assessment meeting

-	Meeting Minutes must be kept

-	Attendance register to be signed by all and kept in Employer File

-	Lethabo Power Station Contractors Safety Meeting (monthly) if on site

-	Departmental Safety Meetings (monthly)if on site

-	Section daily meetings if on site

-	Any meeting requested by the Employer  or Contractor

Regular meetings of a general nature may be convened and chaired by the Supply Manager as follows:

| Title and purpose | Approximate time & interval | Location | Attendance by: |
| --- | --- | --- | --- |
| Risk register and compensation events | Weekly on ________ at ___ |  |  |
| Overall contract progress and feedback | Monthly on _____ at ___ |  | Employer, Contractor and ___ |

- 2.3 Contractor’s management, supervision and key people

- Before work starts on site, an inaugural meeting is held with the Contractor and the Employer, to explain in detail all requirements of the Site Regulations including working hours access to site.

- The Contractor is issued with a file of current Site Regulations on arrival. The file remains the property of the Employer and the Contractor is responsible for its maintenance and updating to include new or revised regulations as issued by the Employer.

- The Contractor must ensure that all personnel performing work on the plant/site are authorised, this includes but not limited to;

	Confine space locations

	Working at heights

	Heat stress areas

	Hazardous substances

- 2.4 Provision of bonds and guarantees

N/A

- 2.5	Documentation control

- Each instruction, certificates, submission, proposal, record, acceptance, notification, reply and other communication which this contract requires is communicated in a form which can be read, copied and recorded.

- Writing is in the language of this contract.

- Assessment supporting documentation to be handed in to the Employer / Service Manager (to be announced by the Employer).

- All communications must be printed and filed in the Service Managers file.

- 2.6 Invoicing and payment

Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Service Manager’s payment certificate.

The Contractor shall address the tax invoice to

•	Name and address of the Contractor and the Service Manager;

•	The contract number and title;

•	Contractor’s VAT registration number;

•	The Employer’s VAT registration number 4740101508;

•	Description of service provided for each item invoiced based on the Price List;

•	Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

•	Purchase order number

•	CPA calculation sheet

•	CPA calculation sheet and the Invoice for CPA (with the GL Account Number and the Cost       Center on the Invoice) to be send to the financial department as per the Employer Invoicing procedure / instruction. Invoices and a Copy of the Assessment with a Service Entry number to be send to the financial department as per the Employer’s  Invoicing procedure / instruction

- 2.7 Contract change management

This section is intended to deal with any additional requirements to the compensation event clauses in section 6 of the core clauses; such as the use of standard forms.

•	Changing the Service Information

•	Access

•	Provision by the Employer

•	Stopping work

•	Work of the Employer or others

•	Reply to communication

•	Changing a decision

•	Withholding acceptance

•	Delayed tests or inspections

•	Change of Affected property

•	Materials, facilities, etc. for tests

•	Employer’s risks

•	Assumption about Compensation Events

•	Employer’s breach of contract

- 2.8 Records of Defined Cost to be kept by the Contractor

N/A

- 2.9 Insurance provided by the Employer

•	Refer to Contract Data section 8.

- 2.10	Training workshops and technology transfer

- The Contractor’s personnel to do safety induction before entering the site and commencing with any work on Employer’s account.

- All training will be on Contractor’s account

- The Contractor’s personnel to have job specific training.

- Contractor Supervisor and Technician to be Authorized in plant safety regulations within 3 months of contract start

- Minimum safety requirements for access is HIRA training

- 2.11	Design and supply of Equipment

- In the case for a Modification the Modification process must be followed.

- Contractor to provide all tools and equipment necessary to perform the required service.

- All equipment and tools needs to be marked and a list off all tools with the identification number to be provided to the Service Manager when entering site.

- All lost equipment and tools to be declared to the Service Manager and full details of incident.

- All test Equipment must be calibrated regularly and certificates must be handed in to Service Manager.

- 2.12	Things provided at the end of the service period for the Employer’s use

- 2.12.1	Equipment

- The Contractor returns to the Employer, equipment and surplus plant and materials provided by the Employer.

- Contractor Provides information and other things as stated in the Service information.

- 2.12.2	Information and other things

- All Reports / Documents to be compiled, filed, discussed and handed over to the Employer (the day to be announced by Employer) and at the end of the service.

- On completion of contract the Contractors safety file will be hand over to the Service Manager and will be saved for 40 Years after completion / termination of the contract.

- Contractor is Responsible to ensure that his Letter of Good standing is valid at all times as stipulated in the construction regulations point 7 (C) (iv) and she specifications 2.5.2 (iv) and 3.10..Contractor  will not be allowed on site if  the Contractors letter of good standing is not valid.

- 2.13 Management of work done by Task Order

- A Task Order is the instruction to commence work.

- No work shall commence until Task order is issued and supported by corrective / planned  maintenance defect and  has been finalised and accepted and signed by both  the Employer and Contractor.

- Completion certificate to be issued after task on Task Order is completed and Assessment certificate to be completed.

- Task orders, Assessments and Completion Certificates will be used for work required.

- All work will be issued via SAP Maintenance or as per Task order system.

- 3. Health and safety, the environment and quality assurance

- 3.1 Health and safety risk management

The Contractor shall comply with the health and safety requirements contained in Annexure SHE Specification 14RISK SRM – 084 to this Service Information.

- All The Employers health and safety procedures and regulations to be adhered to by the Contractor.

- A SHEQ file to be handed in at the SHEQ department for approval prior to wok commencement and kept up to date for the duration of the contract.

SHEQ Policy

Eskom SHEQ Policy

The Employer has made a commitment to conduct business with respect and care for people, the environment and assets and that no operating condition or urgency of service justifies exposing anyone to negative risks arising from the Employer’s business.

Compliance with the Employer’s SHEQ Policy and applicable regulations is the responsibility of every employee and Contractor.

Contractor SHEQ Policy

All Contractors shall have an OHS policy signed by the CEO of the Contractor and prominently displayed where employees normally report for duty.

Signed copy of the OHS policy shall form part of the SHEQ file.

SHE PLAN REQUIREMENTS:-

- Principal Contractors shall develop a suitable and sufficiently documented site specific SHE plans, based on the scope of work and client SHEQ specification.

- The SHE plan must be pre-approved by the client for implementation. The principal Contractor/Contractor has a responsibility to send the SHE plan to the client for approval prior to commencement of work.

- The SHE plan must be applied from the commencement of and for the duration the construction work, which must be updated/reviewed as the work progresses/changes.

When a principal Contractor intends appointing Contractor, the principal Contractor shall ensure that the Contractor provides and demonstrate a suitable, sufficiently documented and coherent site specific health and safety plan, based on the client's SHEQ specifications and scope of work

Health and Safety Arrangements

The Contractor ensures that all his personnel attend a Health and Safety Induction Course prior to contract starting date, and annual re- induction.  The Induction Course is presented by the Employer’s Safety Risk Department at Lethabo Power Station.  Arrangements are made with Safety Risk Management, by the Contractor.

The Employer’s Safety Risk Manager visits and inspects the Contractor’s workplace or site yard and the working areas to ensure that tools; machinery and Equipment comply with the minimum safety requirements.

The Service Manager may instruct the Contractor to stop work, where the Contractor’s personnel fail to conform to safety standards or contravene health and safety regulations.  Such stop-work order is not a compensation event.  The Service Manager may instruct the Contractor to discipline his employees and to submit a disciplinary action report to the Service Manager.  The Contractor implements additional health and safety precautions where necessary.

Health and safety

The Contractor complies with the Occupational Health and Safety Act 85 of 1993, as well as per the Employer’s procedure as stipulated below:

•	SHEQ Policy 32-727

•	The Employer’s  Procurement and Supply Chain Management Procedure 32-1034

•	SHE Requirements for the Employer’s  Commercial Process 32-726

•	Contractor Health and Safety Requirements 32-136

•	Integrated SHE Organization; Roles and Responsibilities and Statutory Appointments 32- 296

•	Live-saving Rules 240-62196227

•	Working at Heights 32-418

•	The Employer’s Vehicle Safety Specifications 32-345

•	Lethabo Contractor SHEQ Specifications 14RISK SRM - 084

Site Regulations and Procedures

Site Regulations

The latest revision Lethabo Power Station Site Regulations form part of this contract.

Copies of these procedures are available on request.

(Any additional site regulations implemented will be applicable)

Safety risk management

“Standard for health and safety at Lethabo Power Station - requirements to be met by Contractors”.

Vehicle and driver safety

All drivers, passengers and pedestrians must obey vehicle safety requirements in terms of the National Road Traffic Act, Act No 93 of 1996, as amended, including other relevant provincial or local requirements.

Speed Limit

All vehicles must be driven with due consideration for personnel and property. All speed limits will be adhered to on the premises at all times.

Transportation of passengers: open LDV’s:

With effect from 31 May 2006 no Employer employee or Contractor would be allowed to transport passengers on the back of open light delivery vehicles (LDV’s).  It is a legal requirement to provide safe transportation of the Employer and Contractor employees – therefore the following will be enforced:

The Employer’s Life Saving Rules:

Five Life Saving Rules have been developed that will apply to all the Employer’s employees, agents, Consultants and Contractors.

•	Rule 1:	Open, Isolate, Test, Earth, Bond, And/Or Insulate before touch - that is any plant operating above 1 000 V.

•	Rule 2:	Hook up at heights - no person may work at height where there is a risk of falling.

•	Rule 3:	Buckle up – no person may drive any vehicle for the Employer’s business and/or on the Employer’s premises: unless the driver and all passengers are wearing seat belts.

The Employer takes a "ZERO TOLERANCE" attitude to drivers and passengers who do not wear safety belts when driving in a vehicle for the Employer’s Business and / or on the Employer’s premises.  The violation of this very important safety rule as well as any safety rule while performing work for or on behalf of the Employer may result in the Employer terminating your obligation to perform work in terms of your contract with the Employer.

All occupants must wear their safety belts properly, and must never put the shoulder belt under their arm or behind their backs.  Drivers and all passengers must buckle-up at all times for the sake of themselves and their families.

•	Rule 4:	Be sober (no person is allowed to work under the influence of drugs and Alcohol.

•	Rule 5:	Use a permit to work – where an authorization limitation exists, no person shall work without the required permit to work.

The Contractor acknowledges that it is fully aware of the requirements of all the above and undertakes to employ only people who have been duly authorised in terms thereof and who have received sufficient safety training to ensure that they can comply therewith.

The Contractor undertakes not to do, or not to allow anything to be done which will contravene any of the provisions of the Act, Regulations or Safety and Operating Procedures.

The Contractor shall appoint a person who will liaise with the Employers Safety Officer responsible for the premises relevant to this contract.

Do safety audits at the Contractor’s premises, its work-places and on its employees;

Refuse any employee, sub-Contractor or agent of the Contractor access to its premises if such person has been found to commit any unlawful act or any unsafe working practice or is found to be not authorised or qualifies in terms of the OHSACT;

Issue the Contractor with a work stop order or a compliance order should Employer become aware of any unsafe working procedures or conditions or any non-compliance with the Act, Regulations and Procedures by the Contractor or any of its employees, sub-Contractors or agents.

The Contractors Health and safety file is to be submitted for approval to the Employers Safety Officer before contract commencement.

All work stoppages called by the Employer to be adhered to

Contractor is Responsible to ensure that his Letter of Good standing is valid at all times as stipulated in the construction regulations point 7 (C) (iv) and she specifications 2.5.2 (iv) and 3.10..Contractor  will not be allowed on site if his letter of good standing is not valid.

First aid and fire fighting

Adequate first aid and firefighting equipment to be provided by the Employer.

All Contractor personnel must have First aid and firefighting training.

Fire extinguishers to be provided by the Contractor.

Fire Precautions

Any tampering with the Employer’s fire equipment is strictly forbidden.

All exit doors, fire escape routes, walkways, stairways, stair landings and access to electrical distribution boards is kept free of obstruction, and are not used for work or storage at any time.  Firefighting equipment must remain accessible at all times.

The Contractor takes the necessary action to safe guard the area to prevent injury and the spreading of the fire.

Security, fire protection and safety

The Contractor shall be responsible for ensuring the security of the works, and of his plant, equipment and materials. To that end he shall make adequate provision for access control, lighting and watchman to the works where required.

Fire protection

The provision of the Employer’s standard NWS 1494 “Fire Prevention and Protection of Contractor’s premises at New Works sites” shall be applicable.

Safety and incident prevention

The Contractor shall implement and maintain an active Site Safety and Accident Prevention Programme in accordance with the Tutuka SHEQ Specifications. The overriding regulations will however be the Occupational Health and Safety Act.

•	Incident Management, Corrective & Prevention Action Procedure to be adhered to – 14Risk IM PC-019

Reporting of accidents

The Employer follows an accident prevention policy that includes the investigation of all accidents involving personnel and property.  This is done with the intention of introducing control measures to prevent a recurrence of the same incidents.  The Contractor is expected to fully co-operate to achieve this objective. The Service Manager must be informed immediately of any incidents. A written report to be submitted to the Employer within 24 Hours of incidents and any damage to property or equipment

NOTE!  This report does not relieve the Contractor of his legal obligations to report certain incidents to the Department of Labour, or to keep records in terms of the Occupational Health and Safety Act, and Compensation for Occupational Injuries and Diseases Act.

Occupational Health and Safety Act 85 0f 1993 – SECTION 37

In accordance with Section 37 (2) of the Act, the Contractor is appointed by the Employer as mandatory to assume Health and Safety duties and responsibilities.  The Contractor ensures compliance with all requirements of the Act and any instruction or notification that enhances those requirements.

The Contractor acknowledges that he is fully aware of all the requirements of the Occupational Health and Safety Act and undertakes to employ only staff who have been duly authorised in terms thereof and who receive sufficient safety training to ensure that they can comply therewith.

The Contractor undertakes not to do, and not to allow anything to be done which will contravene any of the provisions of the Act, Regulations or Safety and Operating Procedures.

The Contractor appoints a person who liaises with the Employer’s Safety Officer, responsible for the premises relevant to the Contract.  The person appointed shall on request:

•	Supply the Employer’s Safety Officer with copies of minutes of all Health and Safety

Committee meetings, whenever required.

•	Supply the Employer’s Safety Officer with copies of all appointments in respect of

employees employed on this contract, in terms of the Act and Regulations and shall notify

the Employer’s Safety Officer of any changes thereto.

The Employer may, at any stage during the duration of this contract:

•	perform safety audits at the Contractor’s premises, its work place and its employees;

•	refuse any employee, Subcontractor or agent of the Contractor access to its premises if

such person is found to commit any unsafe act or any unsafe working practice or is found not

to be duly authorised nor qualified in terms of the Act;

•	Issue the Contractor with an instruction to stop work  should the Employer

become aware of any unsafe working procedure or condition or any non - compliance with

the Act, Regulations and Procedures referred to in the Occupational Health and Safety Act -

85 of 1993 and all Regulations made hereunder as well as all the Employer’s Safety and

Operating   Procedures. Any such instruction is not a compensation event.  Furthermore, no

amendments to the act or the Regulations or reasonable amendment to the Employer’s

Safety and Operating Procedures will entitle the Contractor to claim any additional costs or

time incurred in complying therewith, from the Employer

Safety Regulations of the Employer

The Contractor conforms to the Employer’s Plant Safety Regulations

The Employer makes available to the Contractor, on request, a copy of the latest revision of the Plant Safety Regulations.

- 3.2 Environmental constraints and management

The Contractor shall comply with the environmental criteria and constraints stated in the following:-

All waste from the project must be disposed in a sound environmental manner in accordance with Lethabo Power Station Waste Management Procedure . Oil spillages must be contained and cleaned as per Oil Spill Management procedure. The project must conform to the Employer’s  Environmental Legal and other Requirements and the project must conform to Lethabo Power Station ISO14001 Standard with reference to Lethabo Power Station’s Environmental Management System Manual. All environmental incidents must be dealt with as per the Station’s Incident Management, Corrective and Preventative Procedure and all environmental incidents must be reported to the Environmental Department on site.

Waste shall be removed promptly to the designated disposal area. No stockpiling will be permitted.

•	Domestic waste to the white waste bins

•	Production waste in the marked bins i.e. coal and ash only

•	Paper and cans to their respective recycling bins

•	Contact Civil Engineering for the disposal of building rubble

•	Scrap metal, Wood & Rubber, Redundant Valves, Pipes, Equipment etc. to be placed in the marked bins in the new Salvage Yard. Solvents and cloths used to the Cleaning Bay.

- 3.3 Quality assurance requirements

The Contractor shall be required to demonstrate by means of a Quality Plan that this organisation is so structured that all the requirements of the specification will be properly monitored and controlled.  The Quality Plan and Control procedures are to be carried out in accordance with QM 58.The Quality Control document is to be submitted for approval to Lethabo within three (3) days after order placement by the Contractor.

No work may commence unless the Quality Control document has been approved in writing and a copy submitted to the Service Manager. The Contractor, in conjunction with Lethabo Engineering must sign off all Quality Control documents after completing all work on site. The Contractor to submit a copy of the final signed off document to the Service Manager within 1 week after Completion of each activity or task

•	QCP  and contract quality plan standards as per QM 58 to be adhered to

•	The Contractor must provide Quality Control Plan documents for approval by Eskom Service

Manager performing any activity.

- 4. Procurement

There is a cross reference from the core clause 11.2(6) definition of Disallowed Cost to the Service Information regarding procurement procedures.  This part of the Service Information MUST include any such procedures to be able to administer Disallowed Cost.

- 4.1 People

Skills development and localization will be applied as prescribed by DTI for specific work/task

- 4.1.1 Minimum requirements of people employed

•	All staff required to perform the activities within the works information

•	All relevant personnel  names and titles must be specified to the Service Manager

•	All Contractors personnel specified in this contract to be on site  as per 2.3

•	All new staff to be appointed in writing.

•	Contract Staff are not allowed to work on any other contract.

•	All new staff to do induction training

•	All replacements of staff will be in the same discipline (like an artisan with an artisan with proof of qualifications)

•	All new staff to be approved by Service Manager before entering the site or commencing work

•	All new staff must hand in all qualifications and relevant documentation to the Service Manager

•	When changing personnel a new access to work form to be completed by the Contractor

•	Only required specified approved amount of personnel to be allowed on site, pre-arrange with Service Manager

•	  Contractor to comply with the minimum leave requirements as per Occupational Health and Safety Act

•	  Contractor’s leave to be planned and discussed with contract Manager before such permission will be allowed by Service Manager

Qualifications (Note – the below mentioned will change from time to time based on the skills required per contract)

Minimum qualifications requirements of people employed by the Contractor are as follows:

•	Site Manager –Diploma  with 5 years related experience

•	Civil Technician with experience on structures – National Diploma in Civil Engineering + 3 years related experience

•	Plumber - 2 years relevant experience as stipulated in  this contract  plus trade test

•	Carpenter must have 2 years relevant experience as stipulated in  this contract  plus trade test

•	Welder (as per required code for the activity) must have trade test and 3 years’ experience

•	Bricklayer / Builder  2 years relevant experience as stipulated in  this contract  plus trade test

•	Semi-skilled must be able to speak, read, write and understand English and have a minimum of completed south African  schooling education of grade 10 and has been trained

•	to execute the scope of work as an semi-skilled

•	Fitter must have 2 years relevant experience as stipulated in  this contract  plus trade test with red Seal

•	Labours must have been trained to execute the scope of work

Note

•	Company job description of must be agreed to by both parties

•	All Contractor’s personnel CV’S and proof of certified qualification to be handed in to Service Manager

- 4.1.2 BBBEE and preferencing scheme

•	As per clause Z3 within contract data

- 4.1.3 Procuremet requirement

PPPFA STRATEGY

Indicate the percentage (%) that is allocated to:

Price		80%

BBBEE Status	20%

Designated commodity (Yes/No)		No

- 4.2 Subcontracting

- 4.2.1 Preferred subcontractors

Sub-Contractors will only be allowed with a written permission from the Service Manager

- 4.2.2 Subcontract documentation, and assessment of subcontract tenders

N/A

- 4.2.3 Limitations on subcontracting

•	Only 25% of scope can be sub contracted

- 4.2.4 Attendance on subcontractors

N/A

- 4.3Plant and Materials

- 4.3.1 Specifications

•	The Employer will  have the first option to supply all spares, materials and consumables and if not able Service Manager will request the Contractor to supply all spares, materials and consumables as per the contract

•	The Contractor is not allowed to use any materials or spares for private usage or on other Eskom sites.

•	Where applicable:- All plant spares and materials to be inspected (Quality Checked) before installing at plant.

•	All plant spares and materials to be inspected (Quality checked) before installing at plant.

•	The Contractor must transport, Personnel, spares, tools, material and consumables as requested.

•	Requests to be in writing the day before the material will be needed.

•	Work and QC do be done according to the Employer’s regulations and procedures

•	The Contractor will be responsible for Inspection and Maintenance on equipment

•	The Contractor will be responsible for the safeguarding, care and security of all items whilst in the Contractors custody and control, until Completion of the whole of the works.

•	Contractor must be “able, trained and be prepared” with the necessary PPE, equipment, tools, skills and authorised to handle any equipment, spares, tools and materials related to the scope

- 4.3.2 Correction of defects

•	All Correction within 90 days on the same plant the same work centre will be seen as re-work.

•	Performance Improvement Report (PIR) / Non-conformance Report (NCR) will be issued on the reoccurrence of the re-work on second time of re-work

•	All work done under a permit must be done in accordance with the Employer’s Low Voltage Regulations as stipulated in the hand book on Plant Safety Regulations.  This includes the barricading to cordon-off areas where the Contractor is working and safety signs indicating that men working overhead when doing maintenance and repairs to load / spreading beams.  A copy of the hand book can be given to the Contractor on request

•	Rework occurs when an Equipment or plant has to be worked on again within a given time frame of 0 to 90 days on the same Plant and by the same Work centre, and it will be on the Contractor own cost.

•	All defected spares to be replaced with the permission of the Service Manager / supervisor.

•	As per clause 42 in the NEC3 TSC.

•	In case of rework caused due to the Contractor’s negligence, all costs will be on the Contractor’s account.

•	The Contractor will do corrective and planned maintenance.

•	Defected spares to be replaced  with the permission from the Service Manager / Employer’s Supervisor

- 4.3.3 Contractor’s procurement of Plant and Materials

The  Employer will  have the first option to supply all spares, materials and consumables and if not able Service Manager will request the Contractor to supply all spares, materials and consumables as per the contract

The Contractor will supply its own consumables

- 4.3.4 Tests and inspections before delivery

•	Certified laboratories and test certificates to be handed in to Service Manager

- 4.3.5 Plant & Materials provided “free issue” by the Employer

•	All spares removed and returned to Lethabo premises must be declared at the main entrance where the removal permit for the spares must be shown to the Protective Services personnel

•	All spares needed to be from stores  must be collected by Contractor and taken to required plant

•	All faulty routable items to be taken to stores with necessary documents

- 4.3.6 Cataloguing requirements by the Contractor

N/A

- 5 Working on the Affected Property

This part of the Service Information addresses constraints, facilities, services and rules applicable to the Contractor whilst he is doing work on the Affected Property.

- 5.1 Employer’s site entry and security control, permits, and site regulation

•	Lifesaving rules to be adhered at all times

•	Access is limited and controlled by Plant Safety Regulations requirements.

•	No employee will be allowed to access the plant or to work without access permit issued.

•	All personnel to work on the plant must be registered on the Worker’s Register by the Responsible Person.

•	All personnel must attend induction before working on site and must obtain gate permits via the Service Manager.

•	Each personnel to have an Identification card at all times

•	Unauthorized access to site is prohibited. The personnel are expected to be at their working site area at all times.

•	No recruitment on site or at the main access gates or any of the Employer’s Premises’ is allowed.

•	All activities to comply with the OSHACT and Regulations

•	All activities on plant must be preceded by a plant risk assessment – Risk assessment as per the Employer’s standard, to be current at all times  ( Live Document)

•	All work to be done according to the contraction regulations at all times

- 5.2 People restrictions, hours of work, conduct and records

•	Normal working hours is the Employer’s working hours

Monday to Thursday 07:00-16:15

Friday s 07:00-12:00

•	Contractor’s working hours to be agreed upon.

•	Other hours will be determine as per critical path activities during outages / breakdowns

•	Overtime on as and when required basis, but must be approved by the Service Manager

•	Daily time sheets must be kept up to date of normal time and overtime worked at all times. The Employer’s Contractors time sheets to be used

•	  Overtime to be worked on an as and when required Basis when needed.

•	All overtime worked must comply with the Employer’s rest period  requirements

•	The Contractor must be available for any plant break downs during after hours, weekends and public holidays.  The Contractor must be on site after 1 hour after a phone call is made

- 5.3 Health and safety facilities on the Affected Property

•	Proto-team on each shift

•	Medical Station and relevant staff on Site.

•	Each workshop has a first aid box available.

•	Yearly induction for all personnel.

•	In an emergency the contract supervisor and Service Manager must notified immediately

First aid centre

The Contractor provides a first aid service to his employees and Subcontractors.  In the case where these prove to be inadequate, like in the event of a serious injury,

the Employer’s medical centre and facilities are available.

Outside the Employer’s office hours, the Employer’s first aid services are only available for serious injuries and life threatening situations.

The Employer is entitled, however, to recover the costs from the Contractor for the use of the above Employer’s facilities

- 5.4 Environmental controls, fauna & flora

Environmental management

•	Proper care of the natural environment is important to prevent nuisance and environmental   degradation.

•	All Contractors shall comply with the Employer’s environmental management procedures and Environmental legislation.

•	Environmental incidents shall be reported to the Employer’s Environmental Department as per incident management requirements.

The Contractor is required to ensure that all goods, services or works supplied in terms of the contract conform to all applicable environmental legislation.  Where work is done on the Site, the goods, services or works supplied will also conform to the Employer’s environmental specifications.

Waste Management

•	Waste segregation is important to facilitate recycling of waste. Ensure waste is disposed of in the correct colour bin.

•	Eskom periodically collects waste from the bins for disposal in the correct manner.

•	No waste should be burned or buried on site.

•	Where Eskom and the contractor have agreed that the contractor is responsible for the disposal of its waste, the contractor shall safely dispose of such waste and keep disposal certificates on file.

Types and colours of bins used on site:

•	Yellow bin for domestic waste

•	Orange bin for hazardous waste

•	Maroon bin for scrap

•	Green box for cartridges

•	Blue box for recyclable paper

Radiation protection

The Contractor conforms to the Employer’s procedure OMOP 2049 and OMOP 2051 when performing any industrial radiography.

Hazardous Substances

It is required in terms of the General Administrative Regulation (Regulation 7) of the Act that any manufacturer, importer, seller or supplier of hazardous chemical substances shall supply the receiver, free of charge with sufficient information for the user, to enable the user to introduce the necessary measures as regards the protection of the health and safety of persons.  It is therefore the responsibility of the supplier (dealing directly with the Employer) to supply the information.  If information is not available for whatever reason, the supplier must indicate and give reasons to the Employer.

Handling of waste produced by the Contractor

All waste introduced to and/or produced on the Employer’s premises, by the Contractor, for this contract, must be handled in accordance with the minimum requirements for the Handling and Disposal of Hazardous Waste in terms of Government Legislation as proclaimed by the Department of Water Affairs and Forestry Act 1994 Ref.:BN0621-16296-5.

The Contractor is responsible to appoint a waste coordinator to ensure that all waste produced is handled according to the applicable legislation.

The Contractor is required to ensure that all goods, services or work supplied in terms of the contract conform to all applicable environmental legislation.  Where work is done on the Employer’s site, the goods, services or work supplied also conforms to the Employer’s environmental specifications.

Waste from the cleaning and maintenance of equipment

The Contractor is responsible to contain all waste due to cleaning and maintenance of equipment and disposes of as described below.

Stockpiling of waste

Waste is removed promptly to the designated deposit areas.  No stockpiling is permitted.

Hazardous waste

Waste declared as hazardous substances in terms of the Hazardous Substances Act no 15 of 1973 is the responsibility of the Contractor to ensure safe removal from the property to a registered Class 1 site

Pest Control

•	Only approved herbicides with a low environmental risk shall be used for pest control.

•	Only registered pest controllers may apply herbicides on a commercial basis.

•	Application of herbicides shall be in accordance with the Fertilisers, Farm Feeds, Agricultural Remedies and Stock Remedies Act 36 of 194.

Water Conservation

•	Incidents related to water pollution must be reported to the Employer’s environmental department within 24 hours.

•	Report/fix leaking taps and pipes to save water.

•	Use water sparingly.

•	Chemical substances shall not be disposed of in waste water or storm water drains.

Air Pollution

•	Dust suppression measures must be in place to reduce airborne dust.

•	Noxious and offensive odours arising from work activities shall be adequately controlled.

Ground Pollution

•	Measures to prevent or control ground contamination shall be put in place e.g. drip trays, bund walls.

•	Spill containment, clean-up and ground rehabilitation shall be done as per Lethabo procedures

- 5.5 Cooperating with and obtaining acceptance of Others

It is likely that other Contractors will be working in the same area. Others might however from time to time require limited access to the same area in order to execute maintenance activities and the Contractor is to be accommodating in such instances.

Planning

Programmes are submitted in hard and electronic copy. The software package is MS Projects, Open Plan or equivalent, accepted by the Service Manager.

Monthly progress report

A monthly progress report will be submitted to the Service Manager

Completion

Completion certificate must be submitted on completion of each task order

Requirements for Completion.

Completion is when the Contractor has done all the work, which the Works Information states he is to do by the Completion Date and has corrected notified Defects, which would have prevented the Employer from using the works.

The Site is handed back to the Employer in a condition acceptable to the Service Manager.

- 5.6 Records of Contractor’s Equipment

•	Contractor’s equipment (Cell phones with Camera’s, Computers, Camera’s etc.) to be and signed in at security and  this form needs to be kept for use when items need to leave site

•	All test equipment must be calibrated and tested regularly and certificates must be handed in to the Service Manager for record keeping

•	All equipment and tools needs to be marked and a list off all tools with the identification number to be provided to the Service Manager when entering site.

•	 All lost equipment and tools to be declared to the Service Manager and full details of incident

.

- 5.7 Equipment provided by the Employer

•	For the purpose of expediting the works, the Employer may make facilities and services available to the Contractor as provided at no cost to the Contractor.  The Contractor will not receive any reimbursement or make any change to the beneficial use of the facilities or services.

•	The Employer may allow the Contractor, for the execution of the works, the reasonable use of its workshop, cranes, tools and equipment, provided that the Employer’s own work and business are not interfered with in any manner by such use.  The Contractor shall leave all workshops, cranes, tools and equipment in as good a condition as he found them, fair wear and tear excepted, and shall be liable for any damages by the Employer as a result of any act of negligence by the Contractor, his employees or sub-contractor while using such workshop, cranes, tools and equipment.

•	The Contractor is responsible for the repair, replacement or correction as necessary of all pieces of tools and equipment supplied by the Employer which are damaged and/or lost whilst in the Contractor’s custody and control.

•	The Contractor must ensure that any one of his employees or Sub-contractor, operating hoist equipment belonging to the Employer, is authorised by the Employer.

- 5.8 Site services and facilities

- 5.8.1 Provided by the Employer

The Employer supplies 220 & 380 V AC power supply at existing points for the purpose of the works only.  All installations or equipment complies with all relevant safety regulations and requirements. Contractor is to supply own 220 or 380 VAC extensions.

The Employer may at his own discretion supply any other Plant and Materials as required by the Contractor to provide the services.

Supply of Electricity

•	Under no circumstances is the Contractor or his employees allowed connecting up to any electrical supply without the permission of the Employer.

•	220V AC 50Hz, 30A and 380V, 60A power supplies are available. All installations or equipment connected to a supply of electricity provided free of charge by the Employer must comply with all relevant safety regulations and requirements. Failure to comply with the safety requirements may lead to immediate disconnection.

•	No guarantees of power supply quality are given and power supply breaks of some duration may occur without warning and it shall not be grounds for additional time or compensation

Water

•	Under no circumstances is the Contractor or his employees allowed connecting up to any piped services without the permission of the Employer.

•	The Employer makes available free of charge, potable water as required for the purpose of this Contract. The Employer does not guarantee continuity of supply and in such cases the Contractor makes his own provision for standby supplies to maintain continuity.

•	The Employer makes available, free of charge, demineralized water as required for the works.

•	The variation of pressure in the water supply, or breakdown in the supply, is not considered grounds for additional time or compensation.

Compressed Air

•	Under no circumstances is the Contractor or his employees allowed connecting up to any piped services without the permission of the Employer.

•	The Employer attempts to make available compressed air (oil free & dry and at selected points) to a pressure reaching lows of 620 kPa and highs of 640 kPa. No guarantees of air supply quality are given, and air supply breaks of some duration may occur without warning.

•	The variation of pressure in the air supply, or breakdown in the supply, is not considered grounds for additional time or compensation.

Scaffolding

•	The Employer makes available scaffolding, free of charge to the Contractor.

•	The Contractor will indicate in the program the need for scaffolding, the size thereof, as well as the loading requirements and the duration of use and communicate it to the Employer, on submission of the program.

•	Under no circumstances is the Contractor or his employees allowed to use scaffolding which have not been certified safe for use.

•	The delay in scaffolding, in the event of the Contractor failing to indicate the need thereof in the program, is not considered grounds for additional time or compensation.

Roads

•	All traffic is limited to using existing roads.

•	The Employer recovers any costs from the Contractor that is incurred from damage caused to underground services, structures, etc., as a result of the Contractor not using the prescribed routes.

First Aid Centre

•	Ambulance and first aid facilities are available at a fee on site.

Telecommunications

•	The Contractor arranges with the Employer for the use of telecommunication services. The use and the

cost associated with the telephone will be for the Contractor’s account.

•	Failure to pay the amounts due will result in the Employer deducting the amounts from any tax invoice/ payment certificates, handed in to the Employer for payment.

- 5.8.2 Provided by the Contractor

Roads and Vehicles

•	All vehicles used on site, by the Contractor will be road worthy.

•	All road signs and traffic laws / regulations on site will be adhered to. Employees of the Contractor failing to comply will be removed from site and denied any further access

Security

•	The Contractor is responsible for all security on site, viz. fencing off, night watch and access control in order to secure all plant, materials and the works itself. All these measures must be in accordance with any relevant regulations and standards and subject to the Employer's approval.

•	It is also the Contractors responsibility to ensure the security of all completed portions of the works prior to Completion.

Offices, Workshops and Stores

•	The Employer  provides, erect and maintain for his own use, any additional office accommodation and stores he requires, together with drainage, lighting, heating, and hot and cold water services as required.

•	The Contractor’s site establishment price includes all treatment of the site that he considers necessary for his entire operation throughout his period of occupation and under all weather conditions.

•	The Contractor also includes for all security and access arrangements that he considers necessary.

Sanitary Facilities

The Contractor provides, service, maintain and remove on completion any additional facilities required and allow for it in his Price.

The Contractor’s employees who work with asbestos is not allowed to use the Employer’s ablution  or  messing facilities at the workplace during and after stripping of lagging materials, for fibres that may be attached to workers clothing, or to any other article

Contractor to provide and insure safe transportation services for all his Contractors and it must comply to 32-93 and 33-345 procedures.

•	Contractor to provide own (Coffee, sugar, milk, tea etc.)

•	All computers and printers accessories needed to be provided by the Contractor

•	The Contractor will be responsible for the cost of all private phone calls, faxes and internet usage.

•	The Contractor to provide accommodation and meals for his / her employees and costs for this to be included in the contract price.

•	Contractor to supply home   work home transport  for all employees

•	All PPE to be provided by Contractor.

•	Provide SABS approved Safety harnesses as per the Employer’s Safety Requirements.

•	COC’s to be provided of all LV equipment and Cabins provided by the Contractor.

•	Contractor to provide own tools and equipment and test instruments such as Insulated tools to enable to the Contractor perform work according to the scope of work

•	    Contractor to provide own fire extinguishers for their facilities and vehicles.

•	Contractor will provide a detailed method statement with regard to the scope of work will on

how the Civil maintenance and how structural inspection and repairs will be done

•	Contractor to submit valid police clearance certificates for all Contractor’s personnel.

•	Minimum safety requirements for access is HIRA training

For the Method Statement the Contractor will:

a)	Supply a letter of undertaking that the Contractor does have the correct tools and

equipment to perform the activity, Contractor also to provide a list of tools and equipment   that is  registered on the Company’s register.

b)	QCP’s and Certified Letters to be provided for prove of previous similar activities

done, with references of previous activities done

Personal Protective Equipment

The Contractor supplies, maintains and ensures that his personnel at all times wear personal protective equipment as required per site.

Housekeeping

The Contractor’s Equipment does not impair the operation of the plant or access to the plant.

All debris to be removed from the plant after performing task and Contractor to maintain good housekeeping at all time

Access permits

All applicable Contractor personnel shall be issued with access and vehicle permits (Contractor Permit) which will contain the following information:

	Name

	ID Number

	Company

	Validity date

All Contractor permits must be submitted to Protective Services when the workers leave the Site after Completion of the works.

The Contractor applies with Lethabo Power Station Protective Services for the issuing of permits.

The Contractor submits his application at least 24 hours prior to entering the Security area.  This application form must be delivered to Protective Services, or can be faxed to (017) 749 9168.

The form contains the following information:

	Employee Name.

	Employee ID Number.

	The Employer’s Safety Co-ordinators signature.

	The Employer’s Service Manager’s signature.

	Copy of the first page of the ID book of every employee of the Contractor, photocopied to reduce the size to 65%.

The form is appended to the Contractor’s Safety Manual, referred to in Section 2.3.2 (b).

The Contractor’s visitors and personnel shall conform to the security arrangements in force at the Site at all times.

The Chief of Protective Services may, with valid cause, remove any of the Contractor’s personnel from Site, either temporarily or permanently.  He may deny access to the Site to any person whom, in the opinion of the said Chief of Protective Services, constitutes a security risk.

No unauthorized vehicles will be allowed on Site.  Contract vehicle application should be directed to the Service Manager.

The Contractor will be limited to the working areas associated with the works.  The Contractor is forbidden to enter any other areas, and must ensure that his employees abide by these regulations.

Parking inside the Power Station is allowed. The parking application must be addressed to the protective services. All Contractors will supply protective services with their vehicles registration numbers.

No recruiting of casual labour may be done on Eskom premises, including the area outside the power station security gate.

The Contractor obtains the access procedures, from the Service Manager, which may change depending on the prevailing security situation.

Standby personnel

The Contractor supplies the Service Manager with a standby roster of standby personnel.

Temporary cabling

The Contractor will be provided with all temporary wiring and cabling to lead power from the point of supply to the various points where it is required. The Contractor maintains and removes it on Completion.

- 5.9 Control of noise, dust, water and waste

•	All necessary and relevant PPE must be used at all time when entering or working on plant

•	Risk assessments must be completed before commencing with any task to be current at all times (Live Document)

•	All relevant procedures to be used at all times

- 5.10 Hook ups to existing works

•	The Employer reserves the right to have any of the Contractor’s personnel removed off site without cancelling the contract if, in the Employer’s opinion, it is warranted.

•	The Employer reserves the right to request disciplinary / corrective action if, and when, required.

•	The main Contractor is accountable for the management of their sub-contractors and suppliers and to ensure that the applicable legal and the Employer’s requirements (applicable during contract execution) are complied with by the sub-contractors and suppliers (all tiers).  If there are non-conformances / non-compliance to applicable legal and the Employer’s requirements identified, then the Main Service Provider/Principle Contractor will be penalised.

•	The Contractor shall operate under the direction and instructions of the Employer’s Manager or such person/people as may be appointed by him if not in conflict with the Occupational Health and Safety Act and the Generation Plant and Safety Regulations.

•	The Contractor shall maintain a high standard of workmanship expected by the Employer and shall comply with any quality assurance and quality procedures implemented by the Employer.

•	The Employer reserves the right to have any of the Contractor’s personnel removed off site without any compensation to the Contractor in the event of the Contractor’s personnel being in contravention with the OHS Act or any of the Employers rules, regulations and procedures

•	The Employer reserves the right to terminate the contract, once 3 non-conformances / PIR’s are raised against the Contractor

•	The Employer reserves the right to request disciplinary/corrective action if, and when, required.

•	The Contractor must submit Curriculum Vitae’s of its entire staff prior to work commencing on site.

•	The Contractor must submit certified copies of qualifications and or certificates of its entire staff prior to work commencing on site.

•	The Contractor will be responsible for the full payment of the legislative training costs for every employee at the Contractor’s cost, in the event that the employee have to redo the training due to failing at the first attempt as well as the subsequent attempts that follows until the employee is authorised.

•	All unknown / known services will be brought to the attention of the Contractor by Service Manager. Should the Contractor encounter any other services in the work area, he will immediately bring them to the attention of the Service Manager who will issue instructions as to what actions are to be taken.

•	No welding will be allowed on site unless permission is granted in writing by the Service Manager.

•	The Employer’s carries no responsibility for unforeseen delays unless such a delay is negotiated within 24 hours of the occurrence and written agreement is submitted by the Employer.

•	Care must be taken to prevent damage to any surroundings such as the plant, roads and equipment in and around existing buildings.

•	The Contractor and his employees will be required to conduct themselves at all times in proper and orderly manner while on the Employer’s premises.

•	The Contractor and his employees may only smoke in the allowed / designated areas.

•	The Employer will take immediate steps to institute criminal investigations in the event of any suspected criminal acts e.g. theft etc.

- 5.11 Tests and inspections

- 5.11.1 Description of tests and inspections

The

- 5.11.2 Materials facilities and samples for tests and inspections

Sampling to according to correct standards and as per scope of work

- 6 List of drawings

- 6.1 Drawings issued by the Employer

This is the list of drawings issued by the Employer at or before the Contract Date and which apply to this contract.

Drawing Number¦ Revision ¦Title 0.63/01849 02 General Arrangement of Cation Vessel

0.63/04687 rev 01 and 02 Cation Bottom Regenerant Lateral Details

0.63/04688 rev 01 and 02 Cation Regenerant Collector Details

0.63/01851 02 General Arrangement of Weak Base Vessel

0.63/04699 rev 01 and 02 Weak Base Bottom Collector Lateral Details

0.63/01852 02 General Arrangement of Strong Base Vessel

0.63/4701 rev 01 and 02 Regenerant Collector Strong Base

0.63/4703 01 Strong Base Bottom Distributor

0.63/01853 02 General Arrangement of Mixed Bed Vessel

0.63/4709 01 Bottom Regenerant Distributor Mixed Bed

0.63/4711 01 Top Regenerant Distributor Lateral Details Mixed Bed

0.63/4707 rev 03 Regenerant Collector Mixed Bed

0.63/1854 rev 02 Resin Separation and Cation Regeneration Units

0.63/1855 rev 02 Anion Regeneration Units General Arrangement

- 7 Site procedure

7.1	Permit to Work System

NO work shall be carried out without a "PERMIT TO WORK"

The Contractor’s Responsible Person must satisfy himself that all sources of possible danger are isolated. Details of the Permit to Work system can be found in the Plant Safety Regulations for Lethabo Power Station, Eskom OPR 3305.

A Master Permit to Work is used on declared major outages, details can be found in local procedure LBA 00085. Permit changes are made during the dead time, if it is required by the Contractor that a certain supply be made available or plant tested than this can be applied for at the Outage Management Meeting at least 1 day in advance.

Plant with a prohibitive sign attached may only be operated by appointed Eskom personnel. Any Contractor employee found tampering with such plant will be permanently removed from Site.

7.2	Safety Induction Course

All the employees of the Contractor must attend a safety induction course before they will be allowed to work on the Site. It is the responsibility of the Contractor to ensure that all employees have attended the safety induction.

A list of employees requiring safety induction must be submitted at least 2 days in advance of arrival on site with the date and time of arrival so that the safety induction can be arranged.

7.3	IBI Awareness Techniques

“To prevent incidents and ensure continuous improvement of Lethabo Power Stations business performance in all areas affecting safety, reliability and production, it is expected of all CONTRACTORS service personnel, to attend a three(3) hour training session on Integrated Business Improvement  Awareness, which has to be done as soon as work has commenced;

This is to ensure familiarization and use of error-prevention tools/techniques inclusive of, Pre and Post-job briefs, Risk Assessments, Self-checks (STAR principle), Job observations, Effective communications e.g.3- way, Questioning attitude, Procedural adherence, Hand overs and other related topics.

A monthly IBI scorecard to be completed indicating the use of error prevention tools/ techniques;

The assigned employee fulfilling the role of IBI representative has to attend the IBI representative's forum fortnightly, on Tuesdays, duration one hour.

An IBI representative appointed by the Contractor/Supplier/Consultant to attend the IBI Representative Forum One (1) hour every Tuesday (forth nightly).

IBI Awareness training will be provided by Lethabo Power Station personnel, free of charge, course bookings can be arranged by contacting Rabie Heymans on extension 5040.

7.4	Transportation of passengers: open LDV’s

No Eskom employee or Contractor would be allowed to transport passengers on the back of open light delivery vehicles (LDV’s).

It is a legal requirement to provide safe transportation of Eskom and Contractor employees – therefore the following will be enforced:

All passengers must be transported in a closed vehicle with proper and adequate seating, fitted with safety belt for the number of passengers to be transported.  NO passengers may be transported on the back of a light delivery vehicle (LDV) whether open or closed.

•	Tools and equipment must be properly secured.

•	Only authorized drivers may transport passengers.

•	Proof must be submitted on request in terms of valid roadworthiness of the

vehicle/s.

•	The above must apply to on site and off site transportation of passengers.

7.5	Eskom Life Saving Rules

Five Life Saving Rules have been developed that will apply to all Eskom employees, agents, consultants and contractors.

•	Rule 1:	Open, Isolate, Test, Earth, Bond, And/or Insulate before touch - that is any

plant operating above 1 000 V.

•	Rule 2:	Hook up at heights - no person may work at height where there is a risk of

falling.

•	Rule 3:	Buckle up – no person may drive any vehicle on Eskom business and/or

on Eskom premises: unless the driver and all passengers are wearing seat belts.

•	Rule 4:	Be sober (no person is allowed to work under the influence of drugs and

alcohol.

•	Rule 5:	Use a permit to work – where an authorization limitations exists, no person

shall work without the required permit to work.

Key points

1.	Comply with all relevant life-saving rules at all times

2.	Comply with all relevant safe work procedures

3.	Guard against complacency

4.	Ensure proper work planning and communication between Eskom and Contractor before performing any activity

Always remember:

•	No operating condition or urgency of service can justify endangering a person’s life or causing injury or damage to the environment.

•	Employees/Contractors to follow correct processes when exercising their right of refusal to perform work in an unsafe situation.

7.6	Local Safety Procedures

The Contractor adheres to all local procedures. A list of local procedures are available on request from the Employer

7.7	Incidents / Accidents

Incidents and accidents must be reported and investigated as detailed in LBA 00030. All incidents must also be reported to the Employer within 24 hours.

First aid must be made available either by the Contractor or use can be made of the Lethabo medical centre at a fee. The availability of the Contractor’s own first aid does not relieve the Contractor of his obligation to report and investigate the incident in accordance with Lethabo Procedure.

7.8	Fire Prevention

Fire prevention and protection requirements to which Contractors must comply are detailed in LBA 00030.

7.9 Protective Equipment and Clothing

The Contractor supplies his own personal protective equipment necessary to carry out the works and the Contractor shall ensure that all overalls for his staff have clearly identifying company LOGO's.

The Contractor is also responsible to inspect and maintain such equipment as required in terms of the OHS Act and local procedures..

7.10 Inspection of Equipment

The Contractor’s equipment is inspected by an authorised Eskom employee on arrival at the site.

The following documentation is required to accompany the equipment where applicable: copies of all test certificates and maintenance records.

Lifting equipment and electrical equipment must be marked with a unique number, code or colour code for identification. If the equipment is found to be in an unsatisfactory condition or if insufficient maintenance has been carried out on the equipment then it will not be approved for use on Site. A list of all lifting equipment and electrical equipment must be submitted to the Employer at least 2 days prior to the occupation date. This list must indicate the unique number and description of the equipment.

Training of operators must comply with the Works Information and statutory requirements.

7.11 Documentation

The Contractor is responsible to have the following documentation available on site in accordance with LBA 00030:

•	A copy of the OHS Act.

•	Copies of all site accident report forms as required by the OHS Act.

•	Copies of minutes of health and safety meetings held on site.

•	Copies of inspection reports produced by the accident prevention officer.

•	The type of reports, level of detail and frequency of reporting will be mutually agreed by the Employer and the Contractor during the contract negotiation phase of this agreement. These may change from time to time on request by the Employer.

•	The Contractor to be represented at all Employer safety meetings.

•	The Contractor to be represented at any ad-hoc meetings that may arise in order to address any work progress or safety related matters.

•	Liaison meetings shall be held with the Employer’s Representative or his/her delegate on a monthly basis to discuss any technical details, or concerns.

This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.

Available from Engineering Contract Strategies Tel 011 803 3008 Fax 011 803 3009