## Slide 1: CARMEL PLUTO 275kV Technical Clarification
Alicia Simbudayal
Line Engineering Services
Date: 23/05/2022

## Slide 3: Carmel Pluto 275kV Transmission Line 1 & 2
Locallity :
Affected towers are located in close proximity to Holfontein, West Rand, approximately 16km from Pluto Substation.
Affected Towers
  DX tower affected – sinkhole 2m from surface cracking
  CAR/PLU line 2 Tower 64 – approx. 10m from surface cracking and depression
  TX CP1 T63A/B – appears unaffected at this time
Sinkhole Diameter - vary from approximately 1 meters to 4 meters. All measurements are an approximate figures due to safety concerns around the collapsible soil conditions surrounding the sink holes.
Overall affected area (includes first scour) – 2.2Ha

## Slide 4
Surface cracks and ground depression
Carmel Pluto 275kV Transmission Line 1 & 2
Sink hole
CAR/PLU Line 2 Tower 64

## Slide 5
Sink holes
Carmel Pluto 275kV Transmission Line 1 & 2
Dx Tower
CAR/PLU Line 2 Tower 64

## Slide 6
Carmel Pluto 275kV Transmission Line 1 & 2
Assumption - Sink hole propagation from the original sink hole (Position in Slide 4) being exposed for years.
Original sink hole

## Slide 7
Carmel Pluto 275kV Transmission Line 1 & 2
Farmer filling sink hole edges with surrounding rocks.
Original sink hole

## Slide 8: Scope of Works
Competent Person (SANS 1936:2012) Scope -

## Slide 9: Scope of Works
Scope (SANS, SAICE CoP, governing standards (int & ext))-
  Site Walkover & Desk Study – Contractor to purchase relevant literary information required
  Gravity Survey (Optional)
    2.2Ha
    to determine if piping extends under tower base
    Access may present concerns – Aerial Gravity Survey may be required (discretion of competent person)
  Percussion Drilling
    Minimum 3 x BH

## Slide 10: Scope of Works
Laboratory Testing (if required)
  3 x Foundation Indicator
  3 x Direct Shear
  3 x Double Oedometer
  3 x Permeability & Dispersivity Tests
  6 x CBR MDD (AASHTO)
Sample acquisition as per relevant standards
Use of accredited laboratory

## Slide 11: Remediation Outline
SANS 2001 BE 3
  If mass infill – Contractor to recommend quantity and material sources
  Ancillary works identified (laydowns etc)
  OSH Act
Kleinhans, I., and Van Rooy, J.L., (2016): “Guidelines for Sinkhole and Subsidence Rehabilitation based on Generic Geological Models of a Dolomite Environment on the East Rand, South Africa.”
Supervise execution of remediation

## Slide 12: Deliverables
Technical Report
  Findings
    Classification & description SANS 1936: 2012
    Root cause
    Risk to Infrastructure
    DRMP (where applicable) – monitoring & disaster management, safety measures
    CGS Letter of Comments
    Remediation methodology - SANS 2001 BE 3
  Authorised Person (ORHVS) – present for all works in close proximity to live powerlines – present for duration of works
    Clearances and Equipment Safe Working Heights – SANS 10280, TRMSCAAC, ORHVS

## Slide 13: Literature (incl but not limited to)
SANS 1936:2012, Parts 1-4: Development on Dolomitic Land
SANS 633: Soil profiling and rotary percussion borehole logging in dolomitic land in Southern Africa for engineering purposes
SANS 634: Geotechnical Development for Township Investigations
SANS 2001: BE 3: Repair of Sinkholes and Subsidence in Dolomitic Land
Kleinhans, I., and Van Rooy, J.L., (2016): “Guidelines for Sinkhole and Subsidence Rehabilitation based on Generic Geological Models of a Dolomite Environment on the East Rand, South Africa.”
240-47172520: “The Standard for the Construction of Overhead Powerlines (TRMSCAAC 6.0)
240-114967625: “Operating Regulations for High Voltage Systems (ORHVS)”
SAICE – Code of Practice