## EVEREST THESEUS BoQ
BOQ
GROOTVLEI-THESEUS 1 400KV – TOWER 226 REFURBISHMENT
No | DESCRIPTION | UOM | QTY | RATE | AMOUNT
SECTION 1: PRELIMINARIES AND GENERAL
Bill No.1
1 | Preliminary and General
1.1 | Fixed Costs
1.1.1 | Conditions of Contract | Item | 1
1.1.2 | Site Establishment | Item | 1
1.1.3 | SHEQ Compliance | Item | 1
1.1.4 | Tools & Equipment | Item | 1
1.1.5 | Consumables | Item | 1
1.1.6 | Site De-Establishment | Item | 1
1.2 | Time Related Costs
1.2.1 | Security | Item | 1
1.2.2 | Accomodation | Item | 1
1.2.3 | Supervision and Management | Item | 1
1.2.4 | SHEQ Compliance | Item | 1
1.2.5 | Tools and Equipment | Item | 1
1.2.6 | Company and Head Office overhead costs | Item | 1
SUBTOTAL | Bill No.1
SECTION 2: WORKS TO BE DESIGN, MANUFACTURE,SUPPLY,INSTALL, TEST AND COMMISION AS DETAILED IN THE WORKS INFORMATION AND USER REQUIREMENT/ TECHNICAL SPECIFICATION.
Bill No.2
2 | DESIGNS
2.1 | Design full detailed drawings for approval for the foundation for installation (i.e. preliminary, construction and as built drawings) | Hours | 40
SUBTOTAL | Bill No.2
Bill No.3
3 | FOUNDATIONS
SITE CLEARANCE
3.1 | Clear around tower all bushes grub etc and dispose waste approximately 10m x 10m to work and rehab after work is complete | m2 | 100
EARTHWORKS
3.2 | Confirm soil type - soil nomination | no | 1
3.3 | Open up soil around main leg , and down to existing cap level around leg to depth of bottom old foundation in pickable soil after securing mast and inspect | m3 | 12
3.4 | Backfill and compact around mast in layers not exceeding 300mm to a compactive effort of 93% Mod Aashto (max of 5 blows per 100mm using a DCP). | m3 | 12
SUBTOTAL | Bill No.3
Bill No.4
4 | CONCRETE FORMWORK AND REINFORCEMENT
Preparatory Work
4.1 | Clean and paint existing stub with Bitumastic paint (ABE Ravenol or similar approved). | litres | 5
4.2 | Drill existing cap to 250mm depth, hole diameter of 12mm. Drill about 4 holes on the existing cap, about 50mm from edge on all sides. | No | 4
Apply epoxy wet - to - dry concret epoxy prior to concrete casting to Y10 dowel bars. Length of bar must extend from bottom of drilled holes to 50mm below finished cap level. Insert the bars with epoxy into the drilled holes, ensuring that enough epoxy is used to completely fill the holes. Move bars up and down several times to get good adherence.
4.3 | Scrabble through sides of existing concrete approximately 50mm thick into concrete and applying approved wet to dry bonding liquid / epoxy on existing cap surface as well as dowels and into the holes | m2 | 0.36
Concrete Works
4.4 | Insert Y10 dowel bars held in place by installing R6 stirrups every 250mm, ensuring that the final stirrups must be 50mm below the final new cap level. Use normal binding wire to connect stirrups to new Y10 rebar. | No | 4
4.5 | Construct formwork around the stub, from existing cap level to about 500mm above ground level. | m2 | 2.4
4.6 | Install new foundation Mild and High tensile Steel reinforcement in foundation bases and stub | kg | 86.4
4.7 | Immediately cast new Concrete to extend at least 500mm above ground- Note new support members and Existing leg will be encased. | m3 | 0.72
4.8 | Finish off capping with watershed (slope of new cap should be 1 in 100). | m2 | 1.2
4.9 | Concrete cube testing at an independent laboratory | No | 2
SUBTOTAL | Bill No.4
Bill No.5
5 | STRUCTURAL STEEL WORK
TEMPORARY SUPPORT WORK
5.1 | Temporary support tower leg to be worked on by using suitable structure. (use of special beams and legs to hold tower) (4 towers x 4 legs) | no | 1
5.2 | Set up in position temporary back stays, connect two backstays per leg on concrete sledge with min 3 blocks each approx 1 ton each to secondary support leg. The position of the sledge to be determined by Contractor | no | 1
Supply and Delivery new tower steel members and accessories to site. (Weights inclusive of Fastners and Galvanising)
5.3 | Disconnect old stub from existing leg, support member from Knee point.( elsewhere measured) | no | 4
5.4 | Supply new supporting members leg extension | kg | 760
5.5 | Install new supporting members to new stub (new knee point). | kg | 760
5.6 | Paint with suitable protection material (20L) | no | 1
5.7 | Replace anti-climb devices to towers | no | 1
5.8 | Prepare and stockpile dismantled tower members on a predetermined location for the removal thereof by Eskom | Item | 1
Bill No.6
6 | EARTHING
6.1 | Supply and install 40 x 3mm galvanised strip, as detailed in earthing of Transmission Line Towers. | m | 1.2
SUBTOTAL | Bill No.6
TOTAL AMOUNT (EXCL VAT)