## Slide 1
Kusile Power Station Project Kusile Ash Dump Dirty Dam & Raw Water Reservoir Leakage Detection Sumps Microsoft Teams Clarification Meeting
Date: 19 July 2022

## Slide 2: Background
Project Background
The existing leakage detection sumps at the Ash Dump Dirty Dam (ADDD) were overflowing due to inadequate design capacity and no pumping system being installed to pump water back into the ADDD. This would result in dirty water contaminating the environment. The Raw Water Reservoir (RWR) had no leakage detection sumps installed.
Scope of Work (SOW):
  Lifting Station and pumping system Installation
  Lifting Station and pumping system pumps supply and install with duct foot and guide rails
  Installation of ADDD recirculation piping from pump house to ADDD
  Controls and Instrumentation Design and Installation
  Electrical supply, local control panels and cabling

## Slide 3: LPS - Mechanical Scope
Ash Dump Dirty Dam (ADDD)
The existing two sumps at the ash dump dirty dam are small and were designed for temporary use during construction. These sumps will be repurposed for permanent catchments and submersible pumps will be installed with a small lift out station and duct foot
146838-0UXC-S3387
Raw Water Dam (RWR)
There are no existing sumps for the RWR, and two 10000l storage tank will be installed for capturing the leakage flows from each of the two RWR cells.
146838-0UXC-S3397; 146838-0UXC-S3393

## Slide 4: ADDD Site Plan

## Slide 5: RWR Site Plan

## Slide 6: Electrical
Power Supplies for the ADDD Sump Pumps
These pumps will be supplied from the Ash Dump Dirty Dam Pump Building Mini-sub (02BBS). The electrical scope required to instate these power supplies is as follows:
Feeder MCBs (x2) to be installed in the mini-sub
Supply cables (x2) from the mini-sub to the sump.
Excavations (x1) from the mini-sub to the sump locations.
Local control/starter panels (x4)
Power Supplies for the RWR Sump Pumps
These pumps can be supplied from Mini-sub 03 (00BBN03). The electrical scope required to instate these power supplies is as follows:
Feeder MCBs (x2) to be installed in the mini-sub
Supply cables (x2) from the mini-sub to the sump.
Excavations (x1) from the mini-sub to the sump locations.

## Slide 7: Control & Instrumentation
Supply of Pumps Controls Controller Panel
Each Sump/Tank to be equipped with a level Sensor
The Local comptroller panel (No DCS interface) will be used to control pump operation (Start/Stop) based on sump level monitored by a level sensor.

## Slide 8: Technical - Evaluations
Mandatory Criteria |  | 
1. | Tenderer must submit a signed letter stating full compliance to the scope of works without any exclusions (366-259152) | Provide a signed letter of compliance to Eskom’s requirements/specifications. Demonstrate compliance to the full scope of works.

## Slide 9: Technical – Evaluations continued
Qualitative Criteria |  |  | 
1. LPS Evaluation Criteria |  | Reference to Technical Specification / Tender Returnable | Criteria Weighting (70%)
1.1 | Company's background and experience in construction of mechanical and underground services with mechanical equipment and piping installation construction projects or similar works as detailed in the scope of works. | Specification 366-259152: Section 3.1.1 - 3.1.2. Demonstrate experience on similar projects. Provide Testimonials or Completion Certificates for completed projects consisting of the following information: Name of company where project was executed Project Description Construction period Contract value Contact person | Sub-weighting: 60%

## Slide 10
Qualitative Criteria |  |  | 
1. LPS Evaluation Criteria |  | Reference to Technical Specification / Tender Returnable | Criteria Weighting (70%)
1.2. | Organogram and CV's of key personnel | Provide organogram of key personnel of the main contractor and subcontractors: Organogram should include key personnel as follows(as minimum): Professional Engineer(s) Mechanical, Note: Curriculum Vitae of all key personnel must be included as part of Organogram tender submission. If a subcontractor is appointed, then the tenderer shall demonstrate how tenderer's subcontractor and suppliers shall interface with the tenderer's project team through the organogram | Sub-weighting: 10%

## Slide 11
Qualitative Criteria |  |  | 
1. LPS Evaluation Criteria |  | Reference to Technical Specification / Tender Returnable | Criteria Weighting (70%)
1.3. | Method Statements & Construction Quality Assurance. The Method Statement is to clearly provide details of the construction method to be adopted. The method statements should correlate with the project schedule. | Technical Specification 366-259152: Section 3 to 7. Provide project construction methodology and typical method statements detailing how the Tenderer proposes to execute the Works including de-commissioning, dismantling, transport, design, manufacture, delivery, erection, inspection, testing, commissioning and handover for each activity, including their typical quality control and Inspection test plans : Project construction methodology Loading, Transporting and Offloading of material/plant Piping, supports, pumps and other mechanical equipment erection. | Sub-weighting: 10%

## Slide 12
Qualitative Criteria |  |  | 
1. LPS Evaluation Criteria |  | Reference to Technical Specification / Tender Returnable | Criteria Weighting (70%)
1.3. | Method Statements & Construction Quality Assurance. The Method Statement is to clearly provide details of the construction method to be adopted. The method statements should correlate with the project schedule. | Welding (Steel and HDPE) Excavation/Trenching Welding Pre-casting Grouting and concrete works Hydrostatic testing (Carbon steel and HDPE) Flushing and Cleaning of Piping Asphalt replacement and earthworks (typical method statement and ITP) Steel piping and HDPE Pipe installation and testing (typical method statement and ITP Pump installation and testing (typical method statement and ITP) Lifting and rigging | Sub-weighting: 10%

## Slide 13: Technical – Evaluations continued
Qualitative Criteria |  |  | 
2. Civil & Structural |  |  | weighting: 10%
2.1 | Field Equipment Requirements | Technical Specification: Sections 3.1.4.8.1 and 3.1.4.7 (Table 7). Tender Returnable: Kusile Leakage Detection Project CI Scorecard. | Sub-weighting: 55%
2.2 | Documentation and Drawing Requirements | Technical Specification: Section 3.2.4.1.1.4 (Table 9). Tender Returnable: Kusile Leakage Detection Project CI Scorecard. | Sub-weighting: 45%

## Slide 14: Technical – Evaluations continued
Qualitative Criteria |  |  | 
Electrical Evaluation Criteria |  | Technical Specification 366-213052: Section 3.1.3 & Table 14 | 15%
3.1 | Technical Compliance | Signed letter confirming compliance to the Electrical works (i.e, Technical Specification, Section 3.1.3 - Electrical Design and Installation), and stating all deviations if any. | 5%
3.2 | Technical Schedule A&B | Technical Schedule A&B for all types of power and control cables offered. | 5%
3.3 | Motor Datasheets | All datasheets for the offered motors | 5%

## Slide 15: Technical – Evaluations continued
Qualitative Criteria |  |  | 
4. System Integration Evaluation Criteria |  |  | weighting: 10%
4.1 | Configuration Management Tender /sub-Tenderer to confirm that Plant labelling will be done as per the relevant standards. | Section 3.2.5 | Sub-weighting: 50%
4.2 | Document Management Tenderer/sub-Tenderer provides letter of compliance to Eskom systems and processes i.e. 240-86973501 Engineering Drawing Standard and 240-53114186 Document and Record Management Procedure, as well as compliance to ISO 9001-2015, Quality standard Contractor to provide a letter confirming compliance to the VDSS and the Handover Plan as specified in section 5.3 | Section 3.2.4 | Sub-weighting: 50%

## Slide 16: Technical – Evaluations continued
Qualitative Criteria |  |  | 
System Integration |  |  | 5%
1. | Document Management | Tenderer to confirm compliance to the VDSS Provide Handover Plan in alignment to Handover Specification | Sub-weighting: 50%
2. | Documentation and Records Management | Tenderer shall demonstrate compliance to ISO 9001-2015. Quality standard. The tenderer shall confirm that drawings/documentation will be submitted in the compatible formats as indicated in the works. Tenderer to indicate compliance to Eskom systems and processes i.e. 240-86973501 Engineering Drawing Standard and 240-53114186 Document and Record Management Procedure | Sub-weighting: 50%
Tenderers need to achieve a minimum score of 70% under qualitative criteria in order to be considered for further evaluations.

## Slide 17: Contract
NEC3 PSC3 – Professional Services Contracts
Main Option G: Term based Contract
Duration: 9 Months (to be aligned with construction of Phase 2)
SHEQ Requirements – Compliance to SHEQ spec
Employer Policies and procedures – PA agreement and SSA

## Slide 18: Programme Requirements
Level 2 programme in Primavera P6 format and submitted in electronic XER format together with a PDF copy (including resources)
Activity durations in days
Indicative Finish Dates for some of Key Activities and overall

## Slide 19: Tender closing Date
The deadline for Tender submission is:
Date 19 July 2022 at 10h00
Tenders are to be submitted to the Eskom tender box at the following physical address:
THE TENDER OFFICE
Eskom Holdings SOC Limited
NO.10 Smuts Avenue
Witbank / Emalahleni
Mpumalanga

## Slide 20: Must meet criteria
TENDER RETURNABLES – 1.3 of invitation to Tender
The tenderer must submit the returnables set out hereunder as part of its tender. Returnables that are mandatory for evaluation will result in disqualification if not submitted at tender closing.
Pre- Qualification
Mandatory returnables

## Slide 21
Thank You!