## Risk Identification
General High Level Risk Assessment for High Voltage Overhead Line Construction
# |  |  |  | Current Controls | Accountability | Risk Analysis |  |  | Possible Controls
| Risk Description | What is the Root Cause of the Risk? | What are the Consequences? | Current Controls in place | Who is accountable? | Consequence Criteria | Likelihood | RISK RANKING | Further Tasks/Actions to be undertaken to adequately address the risk | Task/Action Owner
1 | Soil classification. Excavate trial pits for soil nomination. | Use machinery (Excavator/TLB etc) or hand to excavate to a founding depth of approximately 3m if possible. Perform and document the soil profile. Backfill the excavation. The position and number of trial pits should be as shown in TRMSCAAC and documented on the soil nomination list and profile sheet. The backfilling must occur directly after the profiling is completed and before continuing to excavate the next test pit. | - Ground line instability or movement. - Excavations collapsing on assets, people or animals. - Detrimental impact of excavation or excavating on third party services or assets. - Waterlogging of Excavations. - Unrestricted access to, exiting and egressing from excavations. - Work in an unmonitored / unsupervised excavation. - Uncertainty over the stability of the soil. - Inadequate shoring. - Equipment falling into excavation. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Excavation Plan in accordance with CR 13 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor | 4 | D | I |  | Principal Contractor
| Hold | This is an engineering hold point in the inspection and test plan. Until the soil type nomination has been approved by the client, no construction shall continue.
2 | Excavation and pile- or rock anchor drilling. Excavate holes for the structure foundations according to the approved design chosen for the nominated soil profile. | Excavate holes to full dimensions required as per the approved design. Stockpile topsoil separately so as to maintain a clean subgrade. If the bottom of the excavation is below the water table, the water shall be pumped out and the excavation kept dry and free from water during construction. Submit a schedule of structure leg ground levels and proposed leg extensions to the client. Have the approved soil type nomination and appropriate approved foundation designs on site. Excavate as close as is reasonably practicable to the exact dimensions as stipulated in the foundation design applied to the chosen soil nomination. In case of over-excavation the foundation shall be fixed as stipulated in TRMSCAAC. Ensure a clean subgrade. | - Ground line instability or movement. - Excavations collapsing on assets, people or animals. - Detrimental impact of excavation or excavating on third party services or assets. - Waterlogging of Excavations. - Unrestricted access to, exiting and egressing from excavations. - Work in an unmonitored / unsupervised excavation. - Uncertainty over the stability of the soil. - Inadequate shoring. - Equipment falling into excavation. - Unstable soil after blasting. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Excavation Plan in accordance with CR 13 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor | 4 | D | I |  | Principal Contractor
3 | Placing of reinforcing steel, stubs, anchor links. Assemble the reinfrocing steel, stub / anchor and concrete slabs in the excavation. Earth the foundation. | Reinforcing steel shall be fabricated and bent according to approved foundation design drawings. Before placement the steel shall be thoroughly cleaned of mill scale and any coatings that may destroy or weaken the bond. The reinforcing steel shall be placed according to the approved foundation design drawings. The minimum cover to the main reinforcing bars shall be as per TRMSCAAC standard. Cover blocks shall be placed in the botom of the excavation and the bottom steel reinforcing placed on top to ensure the clearance. A concrete slab of 300 x 300 x 75 shall be placed at the bottom of the excavation in the position where the leg stub or anchor plate should sit. The stub or link plate shall be fixed to the rebar so that its position does not change during the pouring of the concrete. The reinforcing shall be properly constructed according to the design and fixed together with 18 guage annealed wires. Connect the earthing wire to the stub with a bolted connection and to the rebar with crosby clamps as per TRMSCAAC standard. Installation of shoring / bracing if neccessary (see CR 13). Retaining clearance to overhead electrical lines during moving of material. Maintaining the minimum cover to the reinforcing steel by use of suitable spacers. Accurate placement of anchor link / stub on appropriate cover block ensuring adequate stability to remain within tolerance of position during casting of concrete. (Use of adequate designed temporary works) Connection of earthing by connecting earth wire lug bolted connection to the stub / anchor link and the opposite end to the reinforcing steel with crosby clamps or suitable approved means. | - Ground line instability or movement. - Excavations collapsing on assets, people or animals. - Detrimental impact of excavation or excavating on third party services or assets. - Waterlogging of Excavations. - Unrestricted access to, exiting and egressing from excavations. - Work in an unmonitored / unsupervised excavation. - Uncertainty over the stability of the soil. - Inadequate shoring. - Equipment falling into excavation. - Unstable soil after blasting. - Upsetting of cranes. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Excavation Plan in accordance with CR 13 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor | 4 | D | I |  | Principal Contractor
| Hold | -
4 | Slump test- and concrete cube samples. Perform slump test. Prepare test cubes. | Perform slump test and prepare cube test samples. Slump tests shall be performed as per SANS 5862 Test cubes shall be prepared in accordance with SANS 5861 | Incorrect handling of concrete may lead to incorrect test results. Possibility of injury, equipment damage Incorrect mixes may lead to incorrect results | Adequate supervision, risk assessment before any task is performed | Principal contractor
| Hold | This is a construction hold point in the inspection and test plan. Until the slump test is performed and concrete cube samples taken, no casting of concrete shall continue. (Repeat and document for each casting)
5 | Cast concrete for first pad of foundation. Cast concrete from the concrete mixer truck into the excavation to cover the first pad of the reinforcing steelwork. | Position the concrete mixer truck. Position the concrete chute and lengthening chutes as needed. Pour the concrete into the excavation to cover the first pad of the foundation in case of a conventional pad and pier foundation. Enter the excavation with vibrators to vibrate the concrete to ensure it removal of voids and adequate compaction. Float concrete surface (finishing). Ensure excavation aproach limit is not exceeded and that additional discharging chute lengthening is used as needed. Ensure sufficient stability of the rebar and stub assembly so that it doesn't shift during the pouring process. Guide the concrete chute during the pouring to ensure even spreading of the concrete over the pad. Vibrate the concrete adequately to ensure removal of voids and good compaction of the concrete. Stop vibrating before separation of aggregate occurs | - Ground line instability or movement. - Excavations collapsing on assets, people or animals. - Detrimental impact of excavation or excavating on third party services or assets. - Waterlogging of Excavations. - Unrestricted access to, exiting and egressing from excavations. - Work in an unmonitored / unsupervised excavation. - Uncertainty over the stability of the soil. - Inadequate shoring. - Equipment falling into excavation. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Excavation plan in accordance with CR 13 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor
| Hold | This is a construction hold point. Until the bottom pad in the pad and pier foundation is adequately cured to support placement of shuttering, no foundation construction shall continue. (Repeat for each casting)
6 | Formwork / shuttering. Place formwork / shuttering in excavation. Seal gaps in shuttering and between shuttering and cast concrete. | Enter excavation on top of adequately cured concrete of the first pad. Position shuttering for the second pad. Shuttering should be lowered into the foundation by a truck-mounted crane or similar equipment. Seal the gaps in the concrete formwork / shuttering with an appropriate waterproof sealant. Check if concrete has adequately cured before entering to ensure no damage to concrete cast in first pad. Ensure excavation aproach limit is not exceeded and that truck mounted crane boom has adequate reach so that the stability of the excavation wall is not compromised. Spacers should be used to ensure adequate coverage over reinforcing steel. Seal the gaps between formwork with a waterproof sealant. | - Ground line instability or movement. - Excavations collapsing on assets, people or animals. - Detrimental impact of excavation or excavating on third party services or assets. - Waterlogging of Excavations. - Unrestricted access to, exiting and egressing from excavations. - Work in an unmonitored / unsupervised excavation. - Uncertainty over the stability of the soil. - Inadequate shoring. - Equipment falling into excavation. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Excavation plan in accordance with CR 13 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference.
7 | Removal of shuttering and backfilling. Remove the shuttering on the foundation. Backfilling of the new foundation's excavation in two phases: Fill up, level and compact the substrate in layers. Fill up, level and compact the topsoil in layers. | Enter excavation on top of cast concrete. Remove shuttering from concrete and evaluate for signs of honeycombing or other non-conformities. Exit excavation and remove shuttering. Fill up, level and compact the substrate in layers. Fill up, level and compact the topsoil in layers. Ensure excavation aproach limit is not exceeded and that truck mounted crane boom has adequate reach so that the stability of the excavation wall is not compromised. Enter excavation and remove shuttering from cured concrete; evaluate for signs of non-conformities. Exit the excavation and pour, level and compact the substrate in layers as per TRMSCAAC. Pour, level and compact the topsoil in layers. Ensure homogenous material is used for backfilling to ensure the best possible degree of compaction and stability. Ensure that the surface level of the backfill shall be at such an elevation that water will not accumulate. | - Ground line instability or movement. - Excavations collapsing on assets, people or animals. - Detrimental impact of excavation or excavating on third party services or assets. - Waterlogging of Excavations. - Unrestricted access to, exiting and egressing from excavations. - Work in an unmonitored / unsupervised excavation. - Uncertainty over the stability of the soil. - Inadequate shoring. - Equipment falling into excavation. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Excavation plan in accordance with CR 13 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference.
8
| Hold | This is an engineering hold point in the inspection and test plan. Until the destruction test of guy wire samples complete with structure- and anchor plate attachment mock-ups has been completed and passed, no construction shall continue.
8 | Structure assembly. Assemble the structure on cribbing on the ground according to the relevant approved structural detail drawings. Tighten, punch and paint bolts. | Offload the structural steel at the structure position. Place cribbing in appropriate selected positions to be able to assemble the structure on the cribbing and off the ground and to be able to assemble the structure plumb and stable. Pick up the members by hand / truck mounted crane, hold in position according to the appropriate approved drawing and bolt together. Punch and paint bolts / nuts. Ensure planned layout of structural section complies with the lifting plan / rigging study of the crane operator / lifting foreman to ensure all sections will be within reach of the crane and be safely lifted into place. Assemble structure steelwork in strict accordance with approved structural drawings. Use adequately sized bolts and nuts. Punch and paint bolts. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Work on an unmonitored / unsupervised structure. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11. - Temporary works in accordance with CR 12. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor
10 |  | Offload the structural steel at the structure position. Place cribbing in appropriate selected positions to be able to assemble the structure on the cribbing and off the ground and to be able to assemble the structure plumb and stable. Pick up the members by hand / truck mounted crane, hold in position according to the appropriate approved drawing and bolt together. Punch and paint bolts / nuts. Ensure planned layout of structural section complies with the lifting plan / rigging study of the crane operator / lifting foreman to ensure all sections will be within reach of the crane and be safely lifted into place. Assemble structure steelwork in strict accordance with approved structural drawings. Use adequately sized bolts and nuts. Punch and paint bolts. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Work on an unmonitored / unsupervised structure. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11. - Temporary works in accordance with CR 12. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor
| Install anti-vandal bolts. | Loosen normal bolts and replace with anti-vandal fastners as per anti-vandal standard. Ensure structural stability while replacing normal bolts with anti-vandal fastners to ensure pieces of the structure doesn't collapse on workers. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Work on an unmonitored / unsupervised structure. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11. - Temporary works in accordance with CR 12. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk mitigation in the separate risk and mitigation reference. | Principal contractor
| Hold | This is an engineering hold point in the inspection and test plan. Until the first of each structure type has been inspected and approved by the client at the construction site, no construction shall continue.
| Hold | This is an engineering hold point in the inspection and test plan. Until a sample of each type of hardware assembly for both the phase- and earth conductor has been inspected at the site camp (assembled as per supplier's drawing and hung from a wooden pole), no construction shall continue.
| Hold | This is an engineering hold point in the inspection and test plan. Until the destruction test of guy wire samples complete with structure- and anchor plate attachment mock-ups has been completed and passed, no construction shall continue.
9 | Structure erection. For a self-supporting structure: Attach slings to structural sections in sequence and lift and attach each section until all sections are attached to the main structure. | Position the mobile crane in a position where it will have adequate reach to all sections of the structure as assembled on the ground. Lift the structure legs and attach to the leg stubs (all bolts fastened) on the foundations. Back-stay the legs to ensure appropriately stable structures before any climbing of the structure to disconnect rigging equipment. Lift the body sections and connect and fasten all bolts to all legs of the structure before climbing and removing rigging equipment. Lift K-frames of structure and connect and fasten all bolts to the body before climbing and removing the rigging equipment. Ensure lever hoists and slings are attached to the top of the K-frames as temporary works for positioning of the structure beam. Lift the structure beam and position onto the K-frames with temporary works. Connect and fasten all bolts before removing rigging equipment. Confirm distance from crane to sections and section weights are within capacity of lifting chart as per rigging study. Earth the crane and make sure all outriggers are on stable soil. Ensure sling capacity for each section weight is adequate as per rigging study. Ensure back-stays are as per design of temporary works. Concrete blocks must be on a wedged sled. Ensure all rigging equipment are certified. All unsecured members must be left hanging vertically | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane. - Inadequate / unsafe rigging practice. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, unsecured steel members must be left hanging vertically - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. - Compliance with anti-vandal standard. - Consider generic risk mitigation regarding cranes including SANS standards. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
10 | For a monopole structure: Hydraulically jack the sections of the pole together. Attach slings to the structure and lift the structure as a whole, position the structure on the flange bolts. Plumb the structure and fasten with bolts. | Use a crane to position sections of the pole on adequate cribbing. Connect the hydraulic jacks to the appropriate jacking lugs on the sections. Jack the sections together in compliance with the approved structure design drawings. Lift the structure into position and plumb the structure on the holding down bolts and bolt the flange according to the design drawings. Climb the structure using the structure ladders and disconnect the crane and rigging equipment. Alternative: Lift the bottom section into position on the holding down bolts; plumb and tighten. Lift the second section over the bottom section and lower into position, connect the hydraulic jacks and rigging equipment onto the appropriate lugs and jack into position according to the approved design requirements. Repeat untill the structure is complete and plumb. Confirm distance from crane to centre pegs, and structure weight is within capacity of lifting chart as per rigging study. Earth the crane and make sure all outriggers are on stable soil. Ensure sling capacity for structure weight is adequate as per rigging study. Ensure all rigging equipment are certified. Ensure the hydraulic jack is of adequate capacity as per structure design requirements. Use cherry picker / bucket trucks of appropriate size to access attachment points and lugs on structure and consider the possible servitude constraints. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane. - Inadequate / unsafe rigging practice. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. - Compliance with anti-vandal standard. - Consider generic risk mitigation regarding cranes including SANS standards. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
14 | Guyed V or guyed cross rope For a guyed V or guyed cross-rope suspension structure: Attach slings to the structure and lift the structure as a whole (complete with hardware and insulators), position the structure on the centre stubs and connect the guy ropes to the anchor links. | Position the mobile crane(s) in a position where it will have adequate reach to position the structure (at tallest attachment point) on the centre pegs while no clashing between the structure and the crane boom will occur when the structure is plumb. Lift the structure while coordinating with the movement of the bottom of the masts towards the centre pegs. Ensure the hardware and insulators and running blocks lift in unisin without snagging on the ground. Lift the structure above the centre pegs and lower onto the pegs. Pull the guy wires towards the corresponding anchor link plates and connect the guy wires and plumb the structure. Climb the structure and disconnect the rigging equipment. Confirm distance from crane to centre pegs, and structure weight is within capacity of lifting chart as per rigging study. Earth the crane and make sure all outriggers are on stable soil. Ensure sling capacity for structure weight is adequate as per rigging study. Ensure all rigging equipment are certified. Come - along clamps must be tested before use by a Competent Person | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane. - Inadequate / unsafe rigging practice. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. - Compliance with anti-vandal standard. - Consider generic risk mitigation regarding cranes including SANS standards. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
| Hold | This is an engineering hold point in the inspection and test plan. Until the first of each structure type erection has been inspected and approved by the client at the construction site, no construction shall continue.
Dressing:
Structure dressing: For self-supporting structure
| Hold | This is an engineering hold point in the inspection and test plan. Until the structure earth footing resistance has been measured, no stringing shall continue.
| Hold | This is an engineering hold point in the inspection and test plan. Until the conductor- and earth wire sample destruction testing has been completed, no stringing shall continue.
Stringing and regulating:
11 | String earth wire and OPGW Pull pilot cable between tensioner- and puller stations. | Position pilot cable on drums at puller station. Connect the pilot cable(s) to a tractor (or adequate pulling vehicle). Underrated lifting equipment being used for conductor pulling / lifting Pull the pilot cable(s) along the the line until it passes underneath supporting structures. Pull at least twice the attachment height past the structure. Come - along slippage, error in reading stringing chart Disconnect the pilot cable(s) from the pulling vehicle and connect to the guide ropes that run through the running blocks. Pull the pilot cable(s) through the running blocks and reconnect the pilot cable to the pulling vehicle. Continue pulling the pilot cable(s) and repeat the process. Create a stringing plan (for approval by the engineer) to check the tension of the conductor that will be pulled, ensure an adequate size pilot cable is used, ensure adequate size- and material running blocks are used. Back-stay the double bull-wheel tensioner and puller to adequately designed back-stays (concrete blocks on a wedged frame) to counter the tension in the conductor as calculated in the stringing plan. Ensure the pilot cable doesn't pass between guy wires as it is pulled as it will damage and cut the guy wire. Back-stay terminal structures to counter the tension in the conductor as calculated in the stringing plan. Angle running blocks and position pull-down running blocks (to counter uplift of pilot cable out of running blocks) as required. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection of pilot cables, headboard and running blocks for the chosen conductor to be strung. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11, come - along must be tested and sinpescted by a competent person before use - Temporary works in accordance with CR 12, SANS 4308-1. Lifting equipment (slings, snatch blocks etc), must be inspected and approved for use by a qualified rigger, stringing chart interpretation to be confirmed with profiler and stringing Supervisor - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation and machinery management plan including earthing measures in accordance with CR 24, IEEE 524. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
12 | String the earth conductor / OPGW | Connect the earth conductor / OPGW to a head board and swivels to ensure possible rotation of the pilot cable while keeping the conductor / OPGW stable. Lift the pilot cable off the ground by gently increasing the tension from the pulling- / winch station. Pull the conductor (under tension and off the ground) from the tensioner station to the puller station. Ensure free movement of the headboard through the running blocks throughout the pulling process. Ensure adequate earthing of the puller- and tensioner and running blocks with running earths and earthing plates for operators to mitigate electrocution caused by electromagnetic- and electrostatic induction. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection of pilot cables, headboard and running blocks for the chosen conductor to be strung. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, SANS 4308-1. - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Communication plan in accordance with SANS 10296, - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
13 | Regulate and clamp in earth conductor and OPGW | Measure the conductor temperature as per TRMSCAAC. Pull the conductor until the tension is as per indication on the stringing- and regulating charts provided by engineering for the associated temperature. Lift the earth conductor / OPGW out of the running block. Disconnect the running block and lower it to the ground. Clamp the earth conductor / OPGW into the hardware clamps / dead-ends and connect to the structure attachment points. Measure conductor temperature as per TRMSCAAC standard. Conductors should be lifted from the running blocks with adequate designed temporary works and closed loop slings to ensure conductors cannot fall to the ground. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection / clear marking of come-along clamps. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, SANS 4308-1. - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference.
14 | Install secondary equipment | Install vibration dampers / aerial warning spheres / bird flight diverters. Vibration damper placement as per supplier specification. | - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Unsupervised work on suspended platform. - Collapse / failure of the suspended platform. - The suspended platform system is not certified for use by a Pr.Eng. / Pr. Tech.. - The suspended platform system does not: - have an operating plan and competent operators. - The outriggers fail. - The stop devices fail. - Is not suspended below the ropes. - Is not thoroughly examined. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Suspended platform in accordance with CR 17. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference.
| Hold | This is an engineering hold point in the inspection and test plan. Until the earth wire and OPGW is strung no stringing of the phase conductor shall continue.
15 | String phase conductor(s) Pull pilot cable between tensioner- and puller stations. | Position pilot cable on drums at puller station. Connect the pilot cable(s) to a tractor (or adequate pulling vehicle). Pull the pilot cable(s) along the the line until it passes underneath supporting structures. Pull at least twice the attachment height past the structure. Disconnect the pilot cable(s) from the pulling vehicle and connect to the guide ropes that run through the running blocks. Come - along slippage, underrated lifting equipment, misintepretation of stringing charts Pull the pilot cable(s) through the running blocks and reconnect the pilot cable to the pulling vehicle. Continue pulling the pilot cable(s) and repeat the process. Create a stringing plan (for approval by the engineer) to check the tension of the conductor that will be pulled, ensure an adequate size pilot cable is used, ensure adequate size- and material running blocks are used. Back-stay the double bull-wheel tensioner and puller to adequately designed back-stays (concrete blocks on a wedged frame) to counter the tension in the conductor as calculated in the stringing plan. Ensure the pilot cable doesn't pass between guy wires as it is pulled as it will damage and cut the guy wire. Back-stay terminal structures to counter the tension in the conductor as calculated in the stringing plan. Angle running blocks and position pull-down running blocks (to counter uplift of pilot cable out of running blocks) as required. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection of pilot cables, headboard and running blocks for the chosen conductor to be strung. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, SANS 4308-1. Come - along and lifting equipment to be inspected and approved for use by competent persons, stringing charts to be discussed with the profiler and Stringing Supervior - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation, including earthing measures and machinery management plan in accordance with CR 24, IEEE 524. - Communication plan in accordance with SANS 10296, - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
16 | String the phase conductor(s) | Connect the conductor(s) to a head board and swivels to ensure possible rotation of the pilot cable while keeping the conductor(s) stable. Lift the pilot cable off the ground by gently increasing the tension from the pulling- / winch station. Pull the conductor(s) (under tension and off the ground) from the tensioner station to the puller station. Create equal tension between all conductors in a bundle. Ensure and document that all conductors in a bundle are from the same machine. Ensure free movement of the headboard through the running blocks throughout the pulling process. Ensure adequate earthing of the puller- and tensioner and running blocks with running earths and earthing plates for operators to mitigate electrocution caused by electromagnetic- and electrostatic induction. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection of pilot cables, headboard and running blocks for the chosen conductor to be strung. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, SANS 4308-1. - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Communication plan in accordance with SANS 10296, - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference.
17 | Regulate and clamp in phase conductor(s) in suspension assemblies. | Measure the conductor temperature as per TRMSCAAC. Pull the conductor until the tension is as per indication on the stringing- and regulating charts provided by engineering for the associated temperature. Lift the phase conductor(s) out of the running block. Disconnect the running block and lower it to the ground. Clamp the conductors into the hardware clamps and connect to the hardware attachment points in suspension clamps. Measure conductor temperature as per TRMSCAAC standard. Conductors should be lifted from the running blocks with adequate designed temporary works and closed loop slings to ensure conductors cannot fall to the ground. Sag conductors with the help of sagging boards and leveling scopes. | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection / clear marking of come-along clamps. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, SANS 4308-1. - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Communication plan in accordance with SANS 10296, - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
18 | Regulate and clamp in phase conductor(s) in strain assemblies. | Attach adequate number of block-and-tackle to the structure cross-arms and to adequately anchored winches on the ground. Attach the tackle to come-along clamps on the conductor. Pull the conductor(s) with the winches and regulate with sagging boards and leveling scopes. Measure and cut the conductor(s) taking into acount the strain assembly and insulator length. Crimp the conductor dead-ends onto the conductors. Attach the conductors to the hardware and insulators and attach to the structure spreading the load evenly across the assembly. Use correct come-along clamps designed for ACSR conductor and suitable for the diameter of conductor used. Measure and document the across flat widths of crimped fittings. Adjust sag adjusters and adjustable extension links to spread loads evenly throughout the assembly and conductors | - Uncontrolled collapse of structure. - Damage of structural members and galvanizing due to poor handling. - Inadequate use of temporary works. - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Upsetting of crane / tensioner / puller. - Inadequate / unsafe rigging practice and backstay of tensioner and puller and structures. - Inadequate selection / clear marking of come-along clamps. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12, SANS 4308-1. - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation, including earthing measures and machinery management plan in accordance with CR 24, IEEE 524. - Communication plan in accordance with SANS 10296, - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
19 | Install secondary equipment. | Install jumper assemblies with rigid spacers as per TRMSCAAC standard. Install spacer dampers. Spacer damper placement as per supplier specification / spacing charts. Measure clearance from the jumpers to the structure to ensure adequate clearance. Crimp jumper flags onto the jumper conductors and attach the jumper flags as per TRMSCAAC standard to the dead-ends. | - Overloading of structural members. - Inadequately maintained structure. - Structure not inspected and certified safe for use. - Unsupervised work on suspended platform. - Collapse / failure of the suspended platform. - The suspended platform system is not certified for use by a Pr.Eng. / Pr. Tech.. - The suspended platform system does not: - have an operating plan and competent operators. - The outriggers fail. - The stop devices fail. - Is not suspended below the ropes. - Is not thoroughly examined. NOTE: Consider the generic risk in the separate risk and mitigation reference. | - Structure plan in accordance with CR 11 - Temporary works in accordance with CR 12. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Suspended platform in accordance with CR 17. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
Demolition / decommision:
20 | Demolition. Remove phase- and earth conductors. | Remove secondary equipment, Unclamp conductors, Cut jumpers. Checking integrity of structure before any work and applying necessary temporary reinforcement. Removing secondary equipment. | - No appointed demolition supervisor. - Uncontrolled collapse of structure due to no detailed structural engineering survey and method statement. - Damage of structure due to poor intermitent supervision. - Parts of the structure overloaded with debris. - Accidental collapse due to inadequate shoring. - Collapse of the structure on a person. - Collapse of adjacent structures affected by the demolition of a structure. - Persons being struck by falling objects. - Collapse of the structure due to overloading by equipment weight. | - Structure plan in accordance with CR 11. - Demolition in accordance with CR 14. - Temporary works in accordance with CR 12, SANS 4308-1. - Cranes, tensioners, pullers in accordance with CR 22, SANS 4308-1, IEEE 524. - Electrical intallation and machinery management plan in accordance with CR 24, IEEE 524. - Communication plan in accordance with SANS 10296. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
21 | Lattice structure demolishion. | Decomission structure in sections. Checking integrity of structure before any work and applying necessary temporary reinforcement. | - No appointed demolition supervisor. - Uncontrolled collapse of structure due to no detailed structural engineering survey and method statement. - Damage of structure due to poor intermitent supervision. - Parts of the structure overloaded with debris. - Accidental collapse due to inadequate shoring. - Collapse of the structure on a person. - Collapse of adjacent structures affected by the demolition of a structure. - Persons being struck by falling objects. - Collapse of the structure due to overloading by equipment weight. | - Structure plan in accordance with CR 11. - Temporary works in accordance with CR 12. - Demolishion in accordance with CR 14. - Cranes in accordance with CR 22. - Electrical intallation and machinery management plan in accordance with CR 24. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
Earth mat connections
22 | Cable trenches from terminal structure to substation earth mat connection point. Build/install cable trenches and ramps in new section | Excavate with mini excavator, install pre cast Kerb. Bond the curbs as per design. Backfilling and compacting. Operating mini excavator Move pre-cast segments into the work site | - Contact with dangerous electrical potential overhead or underground. | - Cat excavator with maximum reach 1.8 m to be used only. - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
23 | Provide bonding from the new structure earthing and the substation earth mat points. Providing earth tails from the earth mat to the future structures. | Excavation to place new earth tails with mini excavator and install earth tails. Crimpets to be used. Maximum lift of any conductive part will be limited to 3 meters from ground level retaining a minimum clearance of 5 m to any conductive part. Approach limit markers (made of nonconductive material) will be introduced with warning labels that indicate the danger of exceeding a height of the marker. The induction of construction vehicle operation and control as anticipated in Construction Regulation 23. | - Contact with dangerous electrical potential overhead or underground. - Electrocution due to potential differences (static or inductive). | - Electrical intallation and machinery management plan in accordance with CR 24 - Compliance with all standards as specified in the applicable Line Specification and latest revision of TRMSCAAC. NOTE: Consider the generic risk in the separate risk and mitigation reference. | Principal contractor
| Construction Earthing | Poor risk assessment - not correctly identifying sources of induction on line being constructed / energisation of plant and equipment | Electrocution | Proper earthing practices as per TRMSCAAC / ORHVS, ORHVS authorised person to check clearances / earthing of plant and equipment | Principal contractor | [5 empty] | Consequence | 6 | III | II | I | I | I
Crossings
| Crossings | failure of crossing structures / netting due to poor design / installation | Collapse of crossing structure, leading to injury to people as well as damage to plant and equipment | Temporary Works Engineer to check structure designs / netting designs / backstay integrity, Risk assessment to be done by a competent person before work starts. | Principal contractor | [6 empty] | 5 | III | II | II | I | I
| Crossings | failure of crossing structures / netting due to poor design / installation | Collapse of crossing structure, leading to injury to people as well as damage to plant and equipment | Use utility type wodpoles to SANS 754, pole length and pole top diameter must be specified in the design for the structures, as well as planting depth. | Principal contractor | [6 empty] | 5 | III | II | II | I | I
| Crossings | Damage to Railway infrastructure due to planting poles at unauthorised places along railway lines | Damage to railway infrastructure (Signalling, electical cables) | Get authorisation for pole positions across the railway line from railway authorities. Railway authorities must authorise crossing method (woodpoles / metal scaffolding etc) | Principal contractor | [6 empty] | 5 | III | II | II | I | I
| Crossings | Damage to crossing structure due to train / vehicle collission on the side of the road / railway line | Collapse of crossing structure, leading to injury to people as well as damage to plant and equipment | Temporary Works Engineer to check structure designs / netting designs / backstay integrity, Risk assessment to be done by a competent person before work starts, install "Chevron" reflective Black and Yellow plates on poles closests to the road / railway line for visibility at night or install reflective barriers for poles at road / rail crossing | Principal contractor | [6 empty] | 5 | III | II | II | I | I
| Crossings | failure of crossing structures / netting due to poor design / installation | Collapse of crossing structure, leading to injury to people as well as damage to plant and equipment | Temporary Works Engineer to check structure designs / netting designs / backstay integrity, Risk assessment to be done by a competent person before work starts. Check backstay design: anchor concrete blocks must be on a sldge dug into the ground to prevent sliding along the ground, backstay assemblies (stay plates, stay rods, shackles etc) must be correctly rated, woodpole anchors must be buried in the ground at the correct depth and hole backfill adequately compacted | Principal contractor | [6 empty] | 5 | III | II | II | I | I
| Crossings | Electrocution / microshocks to people and animals due to live crossings / running in close proximity to energised lines / equipment | Injury / death to people and animals | Temporary Works Engineer to check crossing structure, Risk assessment to be done by a competent person before work starts. Competent Person must supervise work in close proximity to live equipment / energised lines, non - Eskom lines (mines, farms etc) to be crossed live must first be inspected by a Competent Person at the point of crossings to identify any special risks that could be differnt from Eskom overhead lines | Principal contractor | [6 empty] | 5 | III | II | II | I | I
| Crossings | Electrocution / microshocks to people and animals due to live crossings / running in close proximity to energised lines / equipment | Injury / death to people and animals | Temporary Works Engineer to check crossing structure, Risk assessment to be done by a competent person before work starts. Competent Person must supervise work in close proximity to live equipment / energised lines, non - Eskom lines (mines, farms etc) to be crossed live must first be inspected by a Competent Person at the point of crossings to identify any special risks that could be differnt from Eskom overhead lines | Principal contractor | [6 empty] | 5 | III | II | II | I | I
[12 empty] | 2 | IV | IV | III | II | II
[12 empty] | 1 | IV | IV | III | III | III
[13 empty] | 1 | 2 | 3 | 4 | 5
Likelihood
Informative references:
[11 empty] | Occupational Health and Safety Risk Assessment Procedure | [6 empty] | 32-520
Occupational Health and Safety Act, 1993, Construction Regulations, 2014
|  | Commercial Risk - Client stability |  | I
|  | Commercial Risk - Contractual T&C's |  | II
|  | Commercial Risk - Financing |  | III
|  | Commercial Risk - Internal procurement |  | IV
Commercial Risk - Liabilities
Commercial Risk - Partner status
Commercial Risk - Payment terms
Commercial Risk - Subcontracts
Commercial Risk - Termination
External Risk - Exchange rates
External Risk - Force majeure
External Risk - Legislation
External Risk - Market condition
External Risk - Political
External Risk - Pressure groups
External Risk - Regulation
External Risk - Site/facilities
External Risk - Weather
Management Risk - Communication
Management Risk - HS&E
Management Risk - Human Resources
Management Risk - Information
Management Risk - Organisation
Management Risk - Planning
Management Risk - Policy and Procedure
Management Risk - Project mgt
Management Risk - Reputation
Technical Risk - Performance
Technical Risk - Reliability, safety, security
Technical Risk - Requirements
Technical Risk - Scope definition
Technical Risk - Technical interfaces
Technical Risk - Technical processes
Technical Risk - Technology
Technical Risk - Test & acceptance
Note on C10: Paulos Timba: Text in colour is the critical steps
Note on I10: Per Risk Assessment Matrix
Note on I12: Per Risk Assessment Matrix
Note on I13: Per Risk Assessment Matrix
Note on I17: Per Risk Assessment Matrix
Note on I19: Per Risk Assessment Matrix
Note on I20: Per Risk Assessment Matrix
Note on I21: Per Risk Assessment Matrix
Note on I23: Per Risk Assessment Matrix
Note on I24: Per Risk Assessment Matrix
Note on I29: Per Risk Assessment Matrix
Note on I31: Per Risk Assessment Matrix
Note on I33: Per Risk Assessment Matrix
Note on I34: Per Risk Assessment Matrix

## Sheet2 (hidden)
|  | Description | Causes | Impact/Consequence | Current Control in place | Consequence Rating | Likelihood Rating | Risk Rating Level
07 STAKEHOLDER MANAGEMENT | 06-04 Communities | Socio economic conditions of the area 4 weeks delay per incident | Locals demanding employment | work stoppage and violance | Political leadership engaged and recruitment process identified FOCUS TO BE IN THE MOOI RIVER AND ESCORT AREA | 2 | E | II
09 PROJECT MANAGEMENT | 09-04 Scope & Schedule | Poor schedule management onsite | Production plans and operational management is poor onsite Lack of proactive risk management | Unutilised resources and time impact on overall project 12 to 15 months delay | Early warning issued. Contractor recovery program | 5 | D | I
09 PROJECT MANAGEMENT | 09-03 Project Management & Controls | Inadequate supervisory skills and management skills for the construction work | Misalignment of roles and responsibilities | Poor quality and low productivity and production levels. Potential 3 month delay on the project 25% time loss) | NEC screening of candidates. | 3 | D | II
06 HSEC | 08-01 Occupational Health and Safety | SHE Failures | Failure to implement and enforce SHE spec, Legislation and regulations | Fatalities, LTI's, Medicals and damage to works and equipment | Ensure that each individual is aware and coplies with Eskom Cardinal rules and comply with SHE spec, all legislations well as the necessary regulations | 4 | C | II
01 LINE AND SUBSTATION EXECUTION | 01-05 Design Battery Limits | Minimising Tower movements and changes | Line profile is not designed with a line walk down | Tower movements not foreseen Affects free issue materials supply to the contractor. Reducndant towers and line material | Early involvement in the project Walkdowns are occuring 8th to 29th September 2014 | 4 | A | IV
09 PROJECT MANAGEMENT | 09-02 Commercials | Financial Controls on the project | Over booking of time by Eskom Staff | Funds may run out | No control No risk in the development stage (DRA) | 4 | A | IV
07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Land and rights issues on the servitudes not comprehensively complete including All services | Housing relocation because of tribal land Farmer payments Quarry encroached on the servitude | Not able to construct because of houses being on servititudes leading to increased cost and schedule 3 month delay | All Options have been done except for Mondi and awaiting SAPPI | 4 | D | I
09 PROJECT MANAGEMENT | Procurement | Timeous procurement of services and contractors required | Project Execution plan not being adhered to by commercial department | 3 months delay | no control | 3 | D | II
09 PROJECT MANAGEMENT | 07-01 Project Resources | Inadequate QS services during execution not being able to deliver reports | Workload for current resources is stretched | Late payment to contractors which causes interest charges to Eskom | NO applicable current controls | 3 | B | III
09 PROJECT MANAGEMENT | 09-03 Project Management & Controls | Inadequate supervisory skills and management skills for the construction work | Contractors coming through TAP/Panel contracts not experienced should the volume of project in PDP be high | Quality and Project Management Issues Impact on Production yields on projects | NO applicable current controls |  |  | I
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | ECO and EO not identifying risks to EMP in advance (Including Contractor EO) | Inexperience/Lack of proactive checks with regards to EMP compliance before construction | Penalties incurred for non compliance Delays on the project | NO applicable current controls | 2 | C | III
09 PROJECT MANAGEMENT | 10-01 People & Teams | Lack of experience of site management staf from the contractor | Skills Shortage in the industry | Time delays on the project due to poor production planning | NO applicable current controls | 3 | D | II
01 LINE AND SUBSTATION EXECUTION | 01-04 Planning and Scheduling | Eskom and Contractor Scheduling not done adequately | Contractor not providing schedule before the progress meetings Analysis not done one week before | Project timelines are not managed. Time related risks not being mitigated CONTRACT MANAGEMENT CANNOT BE DONE EFFICIENTLY | NO applicable current controls | 3 | D | II
09 PROJECT MANAGEMENT | Procurement | Late delivery of free issue material by Eskom Suppliers | Factory overloaded with orders from various customers Strike action | Inability to supply due to capacity of the supplier Standing time for the construction contractor 3 months delay | NO applicable current controls | 3 | D | II
01 LINE AND SUBSTATION EXECUTION | 01-04 Planning and Scheduling | Quality defects on materials arriving onsite | Eskom factory checks not done with every piece of equipment (Random Checks being done) | 1 month delayy | NO applicable current controls | 3 | B | III
01 LINE AND SUBSTATION EXECUTION | 01-06 Operations?Contractor Management | Contractor quality of material not acceptable | Factory inspection checks not being done adequately | Materials being rejected onsite which causes construction delays | NO applicable current controls | 3 | B | III
09 PROJECT MANAGEMENT | 01-04 Planning and Scheduling | Late shipping of the material to site | Late payment to the supplier Inadequate shipping management | Construction delay | NO applicable current controls | 3 | D | II
07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Access rights agreement to servitudes not granted | Unique to each landowner Land owners not granting access to servitude | Out of sequence work and construction delay | All the land owners have been notified and seen by Eskom Existing Servitude | 2 | B | IV
07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Crop damage during construction | clearing the tower footprint Damage during stringing | Costs to pay landowner for damage and agreement on price | NO applicable current controls | 1 | E | III
07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Work stoppage due to Unresolved existing landowner issues with Eskom | Eskom non payment for fire Damage of land |  | NO applicable current controls | 3 | E | I
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Permission to cross services (Wayleave applications) not obtained | Oversight by lands development Application was not processed by relevant | Workstoppage during construction and possible legal contravention and fines | NO applicable current controls | 2 | A | IV
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | WUL requirements where applicable not done | Oversight by land development during the EIA process and EMP development | Legal contravention and workstoppage one year waiting period | NO applicable current controls | 4 | C | II
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Construction in wetlands if required not obtained on time | Oversight by land development during the EIA process and EMP development | Legal contravention and workstoppage one year waiting period | NO applicable current controls | 3 | C | II
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Authorisations for crossing of rivers and streams not obtained on time | Oversight by land development and Emp process | up to R10million Fine | NO applicable current controls | 3 | C | II
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Housing and service relocation for homes within the servitude under the line or in the tower foot print | Land development did not relocate homes timeously Land owners not compensated Not aware of the house being under the servitude | Time delays if not done on time. | NO applicable current controls | 3 | C | II
06 HSEC | 08-01 Occupational Health and Safety | Building next to existing services such as live lines and fuel lines may cause explsions and electrocution risks | Unidentified existing services Space constraints | Induction study not done Protection of the pipeline need to be assessed by Petronet and Transnet Water pipe | NO applicable current controls | 3 | C | II
06 HSEC | 08-01 Occupational Health and Safety | Crossing over major highways may cause safety and technical issues | Powerline falling on moving due to stringing and failure Preselected line route Inheritant risk of the business | Injury Damage to property Road Blockages | NO applicable current controls | 3 | C | II
06 HSEC | 08-02 Environmental | Illegal waste management or Dumping | Lack of registered legal dumping facilities near construction areas/contractor camp | Obtaining the environmental legal contravention |  | 2 | B | IV
01 LINE AND SUBSTATION EXECUTION | 01-05 Design Battery Limits | Inadequate design information for line swops | Lack fo engineering designs with relevant stakeholders | Time delays and cost implication | NO applicable current controls | 2 | C | III
01 LINE AND SUBSTATION EXECUTION | 01-07 Outage Constraints | Outages for Live Crossings not obtained | Live lines teams not available, Grid not available to switch the line off (EA) | Standing time incured by stringing team Possible Fatalities | NO applicable current controls | 4 | E | I
09 PROJECT MANAGEMENT | 10-05 Commissioning | Availability of sub contractors to execute line swaps due to network constraints for the line Swaps | Workload and outage duration and time of outage | Standing time and delays |  | 3 | D | II
09 PROJECT MANAGEMENT | 10-05 Commissioning | Crossing Dx live lines. Obtaining live line teams and making electrical contact | Availability og live line teams Failure of the crossing mechanisms | electrical contact and delays to the project |  | 4 | C | II
01 LINE AND SUBSTATION EXECUTION | 01-06 Operations?Contractor Management | Live line teams not always available according to project schedules | Limited live line resources available or emergency work | Time delays Cost implication | NO applicable current controls | 4 | C | II
01 LINE AND SUBSTATION EXECUTION | 01-07 Outage Constraints | Terrain not suitable for the installation of scaffolding for live crossings | Inheritant risks for the project | Construction of line is delayed until national control grants an outage. | NO applicable current controls | 3 | C | II
01 LINE AND SUBSTATION EXECUTION | 01-05 Design Battery Limits | Contractor designs not completed timeously for eskom approval |  | Delays | NO applicable current controls | 4 | C | II
06 HSEC | 08-01 Occupational Health and Safety | Theft of barricading of excavations | Theft of steel Lack of detail on the SHEQ Spec | Injury to people Fatality Loss of livestock | NO applicable current controls | 4 | C | II
06 HSEC | 06-04 Communities | Labour strikes by employees | Community protests preventing access to construction areas | Possible Fatalities | NO applicable current controls | 4 | C | II
01 LINE AND SUBSTATION EXECUTION | 01-06 Operations?Contractor Management | Contractors not complying to NEC requirements ito Sub contractors brought onsite | Lack of Governance and training. | Injuries. Incurred expenses due to poor performers | NO applicable current controls | 4 | C | II
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Permits for flora not granted on time | Oversight by resources | Project Delays | NO applicable current controls | 4 | C | II
08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Undocumented and identified Environmental risks not covered in the EIA and EMP (Flora permit requirement | Oversight by resources | Project Delays | NO applicable current controls | 2 | B | IV
[7 empty] | Level 1 | 5 | I
[7 empty] | Level 2 | 22 | II
[7 empty] | Level 3 | 6 | III
[7 empty] | Level 4 | 6 | IV

## Sheet1 (hidden)
03-01 Location | #REF! | 01 LINE AND SUBSTATION EXECUTION | #REF!
03-02 Infrastructure | #REF! |  |  | Fully Effective
03-03 Transport & Logistics | #REF! |  |  | Effective | 1 | A | I | People Effects
11-01 Linking Risks | #REF! |  |  | Partially Effective | 2 | B | II | Environment
11-02 Grid Planning | #REF! |  |  | Not Effective | 3 | C | III | Brand and Reputation
11-03 Transformer | #REF! | 06 HSEC | #REF! |  | 4 | D | IV | Legal and Compliance
11-04 Servitude Planning | #REF! | 07 STAKEHOLDER MANAGEMENT | #REF! |  | 5 | E |  | Project Cost
11-05 Plant Performance | #REF! | 08 LEGAL & REGULATORY | #REF! |  | 6 |  |  | Schedule
11-06 Equipment | #REF! | 09 PROJECT MANAGEMENT | #REF! |  |  |  |  | Quality
11-01 Linking Risks | #REF!
11-02 Grid Planning | #REF!
11-03 Transformer | #REF!
11-04 Servitude Planning | #REF!
11-05 Plant Performance | #REF!
11-06 Equipment | #REF!
11-01 Linking Risks | #REF!
11-02 Grid Planning | #REF!
11-03 Transformer | #REF!
11-04 Servitude Planning | #REF!
11-05 Plant Performance | #REF!
11-06 Equipment | #REF!
08-01 Occupational Health and Safety | #REF!
08-02 Environmental | #REF!
08-03 Permits, Licences, Authorisations | #REF!
08-01 Occupational Health and Safety | #REF!
08-02 Environmental | #REF!
04-01 Marketing Strategy | #REF!
04-02 Pricing | #REF!
04-03 Product Specification | #REF!
04-04 Supply & Demand Forecasts | #REF!
04-05 Shipping, Storage, & Distribution | #REF!
03-01 Location | #REF!
03-02 Infrastructure | #REF!
06-02 Health (Occupational / Public) | #REF!
06-03 Environment | #REF!
06-04 Communities | #REF!
10-01 People & Teams | #REF!
10-02 Operations Strategy | #REF!
10-03 Operations Plan | #REF!
10-04 Operations Input into Design | #REF!
10-05 Commissioning | #REF!
10-06 Operations Readiness | #REF!
10-07 Operations Procedures | #REF!
10-08 Operations Information Management Systems | #REF!
01-07 Outage Constraints | #REF!
06-04 Communities | #REF!
03-03 Transport & Logistics | #REF!
09-01 Strategy | #REF!
09-02 Commercials | #REF!
09-04 Scope & Schedule | #REF!
09-05 Cost Control | #REF!
03-01 Location | #REF!
Procurement | #REF!
07-02 Shareholders | #REF!
07-03 Ownership | #REF!
07-04 Contractual | #REF!
07-05 Government (Local / Prov / National) | #REF!
07-06 NGOs | #REF!
03-03 Transport & Logistics | #REF!
01-01 Resources /Material Management | #REF!
01-02 Geology and Land Rights | #REF!
01-04 Planning and Scheduling | #REF!
01-05 Design Battery Limits | #REF!
01-06 Operations?Contractor Management | #REF!

## Sheet6 (hidden)
Row Labels | Sum of 2
A | 10
Financial Controls on the project | 4
Minimising Tower movements and changes | 4
Permission to cross services (Wayleave applications) not obtained | 2
B | 13
Access rights agreement to servitudes not granted | 2
Contractor quality of material not acceptable | 3
Illegal waste management or Dumping | 2
Inadequate QS services during execution not being able to deliver reports | 3
Quality defects on materials arriving onsite | 3
C | 58
Crossing over major highways may cause safety and technical issues | 3
Authorisations for crossing of rivers and streams not obtained on time | 3
Building next to existing services such as live lines and fuel lines may cause explsions and electrocution risks | 3
Construction in wetlands if required not obtained on time | 3
Contractor designs not completed timeously for eskom approval | 4
Contractors not complying to NEC requirements ito Sub contractors brought onsite | 4
Crossing Dx live lines. Obtaining live line teams and making electrical contact | 4
ECO and EO not identifying risks to EMP in advance (Including Contractor EO) | 2
Housing and service relocation for homes within the servitude under the line or in the tower foot print | 3
Inadequate design information for line swops | 2
Labour strikes by employees | 4
Live line teams not always available according to project schedules | 4
Permits for flora not granted on time | 4
SHE Failures | 4
Terrain not suitable for the installation of scaffolding for live crossings | 3
Theft of barricading of excavations | 4
WUL requirements where applicable not done | 4
D | 30
Availability of sub contractors to execute line swaps due to network constraints for the line Swaps | 3
Eskom and Contractor Scheduling not done adequately | 3
Inadequate supervisory skills and management skills for the construction work | 3 | A
Lack of experience of site management staf from the contractor | 3 | Financial Controls on the project
Land and rights issues on the servitudes not comprehensively complete including All services | 4 | Minimising Tower movements and changes
Late delivery of free issue material by Eskom Suppliers | 3 | Permission to cross services (Wayleave applications) not obtained
Late shipping of the material to site | 3 | B
Poor schedule management onsite | 5 | Access rights agreement to servitudes not granted
Timeous procurement of services and contractors required | 3 | Contractor quality of material not acceptable
E | 8 | Illegal waste management or Dumping
Crop damage during construction | 1 | Inadequate QS services during execution not being able to deliver reports
Outages for Live Crossings not obtained | 4 | Quality defects on materials arriving onsite
Work stoppage due to Unresolved existing landowner issues with Eskom | 3 | C
(blank) |  | Crossing over major highways may cause safety and technical issues
Inadequate supervisory skills and management skills for the construction work |  | Authorisations for crossing of rivers and streams not obtained on time
Grand Total | 119 | Building next to existing services such as live lines and fuel lines may cause explsions and electrocution risks
Construction in wetlands if required not obtained on time
Contractor designs not completed timeously for eskom approval
Contractors not complying to NEC requirements ito Sub contractors brought onsite
Crossing Dx live lines. Obtaining live line teams and making electrical contact
ECO and EO not identifying risks to EMP in advance (Including Contractor EO)
Housing and service relocation for homes within the servitude under the line or in the tower foot print
Inadequate design information for line swops
Labour strikes by employees
Live line teams not always available according to project schedules
Permits for flora not granted on time
SHE Failures
Terrain not suitable for the installation of scaffolding for live crossings
Theft of barricading of excavations
WUL requirements where applicable not done
D
Availability of sub contractors to execute line swaps due to network constraints for the line Swaps
Eskom and Contractor Scheduling not done adequately
Inadequate supervisory skills and management skills for the construction work
Lack of experience of site management staf from the contractor
Land and rights issues on the servitudes not comprehensively complete including All services
Late delivery of free issue material by Eskom Suppliers
Late shipping of the material to site
Poor schedule management onsite
Timeous procurement of services and contractors required
E
Crop damage during construction
Outages for Live Crossings not obtained
Work stoppage due to Unresolved existing landowner issues with Eskom

## Risk Identification (2) (hidden)
Risk Identification Workshop
Ariadne Line and Substation Risks
# | Risk Identification |  |  |  |  | Current Controls | Risk Analysis |  |  |  | Possible Controls
| Risk Category | Risk Sub Category | Risk Description | What is the Root Cause of the Risk? | What are the Consequences? | Current Controls in place | Consequence Criteria | Likelihood | RISK RANKING | Basis for RATING | Further Tasks/Actions to be undertaken to adequately address the risk | Task/Action Owner
1 | 07 STAKEHOLDER MANAGEMENT | 06-04 Communities | Socio economic conditions of the area 4 weeks delay per incident | Locals demanding employment | work stoppage and violance | Political leadership engaged and recruitment process identified FOCUS TO BE IN THE MOOI RIVER AND ESCORT AREA | 2 | E | II | People Effects | Stakeholder engagement before the project begins THE WORKS INFORMATION MUST HAVE EMPLOYMENT AS A CONDITION OUT OF SEQUENCE WORK ESTABLISHMENT OF STEERING COMMMITTEES REPRESENTING Community | Bheki Hlengwa
2 | 09 PROJECT MANAGEMENT | 09-04 Scope & Schedule | Poor schedule management onsite | Production plans and operational management is poor onsite Lack of proactive risk management | Unutilised resources and time impact on overall project 12 to 15 months delay | Early warning issued. Contractor recovery program | 5 | D | I | Schedule | Range Analysis to be arranged with DRA Set minimum requirements for key personnel into the requirements Implement delay damages (Higher penalties 10% of the contract withinn three months) for delays by contractor Ensure a resource loaded schedule exists and communicated onsite with the site manager Audits to ensure the resources are mathcing the schedule | Project Manager
3 | 09 PROJECT MANAGEMENT | 09-03 Project Management & Controls | Inadequate supervisory skills and management skills for the construction work | Misalignment of roles and responsibilities | Poor quality and low productivity and production levels. Potential 3 month delay on the project 25% time loss) | NEC screening of candidates. | 3 | D | II | Quality | Interviews and screening of individual cv's. Checking the cv of Key Staff at contractor level | Bheki Hlengwa
4 | 06 HSEC | 08-01 Occupational Health and Safety | SHE Failures | Failure to implement and enforce SHE spec, Legislation and regulations | Fatalities, LTI's, Medicals and damage to works and equipment | Ensure that each individual is aware and coplies with Eskom Cardinal rules and comply with SHE spec, all legislations well as the necessary regulations | 4 | C | II | People Effects | LTIFR 0.5 from 0.35. >50% escalation on target. New construction regulation implemented | Bheki Hlengwa
5 | 01 LINE AND SUBSTATION EXECUTION | 01-05 Design Battery Limits | Minimising Tower movements and changes | Line profile is not designed with a line walk down | Tower movements not foreseen Affects free issue materials supply to the contractor. Reducndant towers and line material | Early involvement in the project Walkdowns are occuring 8th to 29th September 2014 | 4 | A | IV | Project Cost | Project Managers Risk Assessment on the Design before the BOQ | Bheki
6 | 09 PROJECT MANAGEMENT | 09-02 Commercials | Financial Controls on the project | Over booking of time by Eskom Staff | Funds may run out | No control No risk in the development stage (DRA) | 4 | A | IV | Project Cost | SLA between different depts on time allocated per task Performance should be also included in the SLA.(Grid work) Record to be available for acces control (Signing in and signing out) Cost Engineer to provide a time allocation report REQUEST AN OFFICIAL BUDGET FROM THE GRID | Bheki
7 | 07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Land and rights issues on the servitudes not comprehensively complete including All services | Housing relocation because of tribal land Farmer payments Quarry encroached on the servitude | Not able to construct because of houses being on servititudes leading to increased cost and schedule 3 month delay | All Options have been done except for Mondi and awaiting SAPPI | 4 | D | I | Financial Impact | Await for letters for payment made by SAPPI. Require payment for maintenance of servitude before agreement Encroaching housing on the servitude. Meeting with Negotiators to request plans and to mitigate the risk (A few houses). Mine encroached | Project Manager
8 | 09 PROJECT MANAGEMENT | Procurement | Timeous procurement of services and contractors required | Project Execution plan not being adhered to by commercial department | 3 months delay | no control | 3 | D | II | Financial Impact | Utilisation of the panel system
9 | 09 PROJECT MANAGEMENT | 07-01 Project Resources | Inadequate QS services during execution not being able to deliver reports | Workload for current resources is stretched | Late payment to contractors which causes interest charges to Eskom | NO applicable current controls | 3 | B | III | Schedule | Senior Management restructuring | Bheki/Sugan
10 | 09 PROJECT MANAGEMENT | 09-03 Project Management & Controls | Inadequate supervisory skills and management skills for the construction work | Contractors coming through TAP/Panel contracts not experienced should the volume of project in PDP be high | Quality and Project Management Issues Impact on Production yields on projects | NO applicable current controls | 4 | D | I | Financial Impact | Stipulated reuqirements for key personnel | Project Manager
11 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | ECO and EO not identifying risks to EMP in advance (Including Contractor EO) | Inexperience/Lack of proactive checks with regards to EMP compliance before construction | Penalties incurred for non compliance Delays on the project | NO applicable current controls | 2 | C | III | Environment | Reserve rights not to pay the EO monthly cost in the BOQ | Bheki/Sugan
12 | 09 PROJECT MANAGEMENT | 10-01 People & Teams | Lack of experience of site management staf from the contractor | Skills Shortage in the industry | Time delays on the project due to poor production planning | NO applicable current controls | 3 | D | II | Environment | NEC document to include provision of key personnel as well resource loaded schedule | Bheki/Sugan
13 | 01 LINE AND SUBSTATION EXECUTION | 01-04 Planning and Scheduling | Eskom and Contractor Scheduling not done adequately | Contractor not providing schedule before the progress meetings Analysis not done one week before | Project timelines are not managed. Time related risks not being mitigated CONTRACT MANAGEMENT CANNOT BE DONE EFFICIENTLY | NO applicable current controls | 3 | D | II | Schedule | Witholding payment for schedule not being done | Bheki/Sugan
14 | 09 PROJECT MANAGEMENT | Procurement | Late delivery of free issue material by Eskom Suppliers | Factory overloaded with orders from various customers Strike action | Inability to supply due to capacity of the supplier Standing time for the construction contractor 3 months delay | NO applicable current controls | 3 | D | II | Schedule | Once procurement department has issued the supplier to be used, project management to engage supply to agree on a delivery schedule. | Bheki/Sugan
15 | 01 LINE AND SUBSTATION EXECUTION | 01-04 Planning and Scheduling | Quality defects on materials arriving onsite | Eskom factory checks not done with every piece of equipment (Random Checks being done) | 1 month delayy | NO applicable current controls | 3 | B | III | Schedule |  | Bheki/Sugan
16 | 01 LINE AND SUBSTATION EXECUTION | 01-06 Operations?Contractor Management | Contractor quality of material not acceptable | Factory inspection checks not being done adequately | Materials being rejected onsite which causes construction delays | NO applicable current controls | 3 | B | III | Project Cost | Early warning system for steel rejected. Cost to be incured by the contractor. Reflect the delay into the schedule | Bheki/Sugan
17 | 09 PROJECT MANAGEMENT | 01-04 Planning and Scheduling | Late shipping of the material to site | Late payment to the supplier Inadequate shipping management | Construction delay | NO applicable current controls | 3 | D | II | Project Cost | Proper planning and scheduling as per the phases of the project | Bheki/Sugan
18 | 07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Access rights agreement to servitudes not granted | Unique to each landowner Land owners not granting access to servitude | Out of sequence work and construction delay | All the land owners have been notified and seen by Eskom Existing Servitude | 2 | B | IV | Legal and Compliance | Farmer union committee involvement | Bheki/Sugan
20 | 07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Crop damage during construction | clearing the tower footprint Damage during stringing | Costs to pay landowner for damage and agreement on price | NO applicable current controls | 1 | E | III | Project Cost | Case by case management utilising CE | Bheki/Sugan
21 | 07 STAKEHOLDER MANAGEMENT | 01-02 Geology and Land Rights | Work stoppage due to Unresolved existing landowner issues with Eskom | Eskom non payment for fire Damage of land | Delays up to 6 months | NO applicable current controls | 3 | E | I | Schedule | Dx outstanding issues with landowners Escalate to Dx GM and Sifiso, look to settle immediately | Project Manager
22 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Permission to cross services (Wayleave applications) not obtained | Oversight by lands development Application was not processed by relevant | Workstoppage during construction and possible legal contravention and fines | NO applicable current controls | 2 | A | IV | Legal and Compliance | Application are being made at DRA stage | Bheki/Sugan
23 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | WUL requirements where applicable not done | Oversight by land development during the EIA process and EMP development | Legal contravention and workstoppage one year waiting period | NO applicable current controls | 4 | C | II | Legal and Compliance |  | Bheki/Sugan
24 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Construction in wetlands if required not obtained on time | Oversight by land development during the EIA process and EMP development | Legal contravention and workstoppage one year waiting period | NO applicable current controls | 3 | C | II | Legal and Compliance |  | Bheki/Sugan
25 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Authorisations for crossing of rivers and streams not obtained on time | Oversight by land development and Emp process | up to R10million Fine | NO applicable current controls | 3 | C | II | Legal and Compliance | A the EMP stage, applications can be made for a temporary stream crossing During walk downs, record all stream crossings to be submitted for the application Commence with application process during DRA | Bheki/Sugan
26 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Housing and service relocation for homes within the servitude under the line or in the tower foot print | Land development did not relocate homes timeously Land owners not compensated Not aware of the house being under the servitude | Time delays if not done on time. | NO applicable current controls | 3 | C | II | Legal and Compliance | Land Development needs to relocate homes and services timeously. | Bheki/Sugan
27 | 06 HSEC | 08-01 Occupational Health and Safety | Building next to existing services such as live lines and fuel lines may cause explsions and electrocution risks | Unidentified existing services Space constraints | Induction study not done Protection of the pipeline need to be assessed by Petronet and Transnet Water pipe | NO applicable current controls | 3 | C | II | Project Cost | Earths to be installed right through (induction) | Bheki/Sugan
28 | 06 HSEC | 08-01 Occupational Health and Safety | Crossing over major highways may cause safety and technical issues | Powerline falling on moving due to stringing and failure Preselected line route Inheritant risk of the business | Injury Damage to property Road Blockages | NO applicable current controls | 3 | C | II | Project Cost | Special scaffolding used, Diversion of traffic Contractor to provide specific method Traffice authorities to be notified of possible road traffic blockades | Bheki/Sugan
29 | 06 HSEC | 08-02 Environmental | Illegal waste management or Dumping | Lack of registered legal dumping facilities near construction areas/contractor camp | Obtaining the environmental legal contravention |  | 2 | B | IV | Brand and Reputation | Write it in the works information Contractor to provide a list of approved dumping sites at tender stage in accordance with the EMP | Bheki/Sugan
30 | 01 LINE AND SUBSTATION EXECUTION | 01-05 Design Battery Limits | Inadequate design information for line swops | Lack fo engineering designs with relevant stakeholders | Time delays and cost implication | NO applicable current controls | 2 | C | III | Schedule | PM to corodinate the activity with stipulated meetings Line engineering to provid design at tender stage Line designs to be completed two weeks after the walk down | Bheki/Sugan
33 | 01 LINE AND SUBSTATION EXECUTION | 01-07 Outage Constraints | Outages for Live Crossings not obtained | Live lines teams not available, Grid not available to switch the line off (EA) | Standing time incured by stringing team Possible Fatalities | NO applicable current controls | 4 | E | I | Legal and Compliance | Outage management plans submitted within the normal time frames | Project Manager
| 09 PROJECT MANAGEMENT | 10-05 Commissioning | Availability of sub contractors to execute line swaps due to network constraints for the line Swaps | Workload and outage duration and time of outage | Standing time and delays |  | 3 | D | II | Schedule | Proper planning and scheduling as per the phases of the project
| 09 PROJECT MANAGEMENT | 10-05 Commissioning | Crossing Dx live lines. Obtaining live line teams and making electrical contact | Availability og live line teams Failure of the crossing mechanisms | electrical contact and delays to the project |  | 4 | C | II | Project Cost
34 | 01 LINE AND SUBSTATION EXECUTION | 01-06 Operations?Contractor Management | Live line teams not always available according to project schedules | Limited live line resources available or emergency work | Time delays Cost implication | NO applicable current controls | 4 | C | II | Project Cost | Contractor to use private live line team authorisd and assessed. Approved by the grid Live line team to be included in the BOQ for KZN grid | Bheki/Sugan
35 | 01 LINE AND SUBSTATION EXECUTION | 01-07 Outage Constraints | Terrain not suitable for the installation of scaffolding for live crossings | Inheritant risks for the project | Construction of line is delayed until national control grants an outage. | NO applicable current controls | 3 | C | II | Schedule | Outage planning to be done in advance Sequencing of work to suit the outage constraint Checked during the line walkdown | Bheki/Sugan
36 | 01 LINE AND SUBSTATION EXECUTION | 01-05 Design Battery Limits | Contractor designs not completed timeously for eskom approval |  | Delays | NO applicable current controls | 4 | C | II | Schedule | Contractor to nominate whothe design engineers to submit designs. Add in the works info | Bheki/Sugan
37 | 06 HSEC | 08-01 Occupational Health and Safety | Theft of barricading of excavations | Theft of steel Lack of detail on the SHEQ Spec | Injury to people Fatality Loss of livestock | NO applicable current controls | 4 | C | II | Legal and Compliance | Contractors to take photos that the barricading was in place | Bheki/Sugan
38 | 06 HSEC | 06-04 Communities | Labour strikes by employees | Community protests preventing access to construction areas | Possible Fatalities | NO applicable current controls | 4 | C | II | Legal and Compliance |  | Bheki/Sugan
39 | 01 LINE AND SUBSTATION EXECUTION | 01-06 Operations?Contractor Management | Contractors not complying to NEC requirements ito Sub contractors brought onsite | Lack of Governance and training. | Injuries. Incurred expenses due to poor performers | NO applicable current controls | 4 | C | II | Project Cost | List all contractors upfront and approve contractors before use | Bheki/Sugan
40 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Permits for flora not granted on time | Oversight by resources | Project Delays | NO applicable current controls | 4 | C | II | Project Cost |  | Bheki/Sugan
41 | 08 LEGAL & REGULATORY | 08-03 Permits, Licences, Authorisations | Undocumented and identified Environmental risks not covered in the EIA and EMP (Flora permit requirement | Oversight by resources | Project Delays | NO applicable current controls | 2 | B | IV | Project Cost | Walk down to address BHEKI ONE IS HIGH | Bheki/Sugan
| Control Adequacy Assessment |  |  | RBS |  | Risk Matrix
| None |  |  | Commercial Risk - Client stability |  | I
| Totally Ineffective |  |  | Commercial Risk - Contractual T&C's |  | II
| Ineffective |  |  | Commercial Risk - Financing |  | III
| Partially Effective |  |  | Commercial Risk - Internal procurement |  | IV
| Fully Effective |  |  | Commercial Risk - Liabilities
Commercial Risk - Partner status
Commercial Risk - Payment terms
Commercial Risk - Subcontracts
Commercial Risk - Termination
External Risk - Exchange rates
External Risk - Force majeure
External Risk - Legislation
External Risk - Market condition
| Consequence Criteria |  |  | External Risk - Political
| 1 |  |  | External Risk - Pressure groups
| 2 |  |  | External Risk - Regulation
| 3 |  |  | External Risk - Site/facilities
| 4 |  |  | External Risk - Weather
| 5 |  |  | Management Risk - Communication
| 6 |  |  | Management Risk - HS&E
Management Risk - Human Resources
Management Risk - Information
Management Risk - Organisation
Management Risk - Planning
Management Risk - Policy and Procedure
Management Risk - Project mgt
Management Risk - Reputation
Technical Risk - Performance
Technical Risk - Reliability, safety, security
Technical Risk - Requirements
Technical Risk - Scope definition
Technical Risk - Technical interfaces
Technical Risk - Technical processes
Technical Risk - Technology
Technical Risk - Test & acceptance
Note on J10: Per Risk Assessment Matrix
Note on J11: Per Risk Assessment Matrix
Note on J12: Per Risk Assessment Matrix
Note on J13: Per Risk Assessment Matrix
Note on J14: Per Risk Assessment Matrix
Note on J15: Per Risk Assessment Matrix
Note on J16: Per Risk Assessment Matrix
Note on J17: Per Risk Assessment Matrix
Note on J18: Per Risk Assessment Matrix
Note on J19: Per Risk Assessment Matrix
Note on J20: Per Risk Assessment Matrix
Note on J21: Per Risk Assessment Matrix
Note on J22: Per Risk Assessment Matrix
Note on J23: Per Risk Assessment Matrix
Note on J24: Per Risk Assessment Matrix
Note on J25: Per Risk Assessment Matrix
Note on J26: Per Risk Assessment Matrix
Note on J27: Per Risk Assessment Matrix
Note on J28: Per Risk Assessment Matrix
Note on J29: Per Risk Assessment Matrix
Note on J30: Per Risk Assessment Matrix
Note on J31: Per Risk Assessment Matrix
Note on J32: Per Risk Assessment Matrix
Note on J33: Per Risk Assessment Matrix
Note on J34: Per Risk Assessment Matrix
Note on J35: Per Risk Assessment Matrix
Note on J36: Per Risk Assessment Matrix
Note on J37: Per Risk Assessment Matrix
Note on J38: Per Risk Assessment Matrix
Note on J39: Per Risk Assessment Matrix
Note on J40: Per Risk Assessment Matrix
Note on J41: Per Risk Assessment Matrix
Note on J42: Per Risk Assessment Matrix
Note on J43: Per Risk Assessment Matrix
Note on J44: Per Risk Assessment Matrix
Note on J45: Per Risk Assessment Matrix
Note on J46: Per Risk Assessment Matrix
Note on J47: Per Risk Assessment Matrix
Note on J48: Per Risk Assessment Matrix
Note on J49: Per Risk Assessment Matrix