## Technical Schedule
Technical schedules A and B for 6.6 kV NEC, 2000A for 10s and 140A continuous_Hendrina PS
Eskom Material Number: xxxxxx
Schedule A: Purchaser's specific requirements
Schedule B: Guarantees and technical particulars of equipment offered
According to Specification : 240-57648848
1 | 2 | 3 | 4 | 5
Item | Description |  | Schedule A | Schedule B
1 | Identification
| a) Supplier’s name |  | xxxxxxxxxx
| b) Manufacturer’s name |  | xxxxxxxxxx
| c) Type designation |  | xxxxxxxxxx
2 | Site conditions
| a) Altitude | m | £1800
| b) Maximum ambient temperature | oC | 45
| c) Minimum ambient temperature | oC | -10
| d) Maximum diurnal variation | oC | 35
| e) Yearly Daily Average | oC | 25
| f) Intensity of solar radiation | kW/m2 | 2.5
| g) Relative humidity | % | £ 100
3 | Electrical conditions
| a) Nominal system voltage | kV | 6.6
| b) Maximum system voltage | kV | 7.2
| c) Nominal frequency | Hz | 50
4 | Rated requirements
| a) Nominal short time (10 s) current of NEC | (r.m.s.)A | 2000
| b) Nominal continuous current of NEC | (r.m.s.)A | 140
| c) Zero sequence reactance (Xo) | W/ph | 5.273
| d) Zero sequence resistance (Ro) at 100oC | W/ph | N/A
| e) Zero sequence impedance (Zo) at 100oC | W/ph | 5.273
4.1 | NEC
| a) Zero sequence reactance (Xc) | W | xxxxxxxxxx
| b) Zero sequence resistance (Rc) at 100oC | W | xxxxxxxxxx
| c) No load loss of NEC at Un | kW | xxxxxxxxxx
| d) Flux density of NEC core | T | xxxxxxxxxx
| e) Magnetization current | (r.m.s.)A | xxxxxxxxxx
| f) Current density at nominal short time current | A/mm2 | xxxxxxxxxx
4.2 | NER |  | xxxxxxxxxx
| a) Zero sequence reactance (Xr) | W | N/A
| b) Zero sequence resistance (Rr) at 100 oC | W | N/A
| c) Nominal voltage (Un/Ö3) | kV | N/A
| d) Temperature coefficient at 100 oC | W/oC | N/A
| e) Specific heat capacity | kJ/kg oC | N/A
| f) Temperature range in which (d) and (e) apply | oC | N/A
4.3 | Auxiliary transformer
| a) Nominal rating | kVA | N/A
| b) Primary nominal voltage | kV | N/A
| c) No load secondary voltage | V | N/A
| d) Vector group Dyn11 or Yzn11 |  | N/A
| e) Flux density of aux core | T | N/A
| f) Magnetizing current | A | N/A
| g) Load loss | kW | N/A
| h) No-load loss | kW | N/A
| i) Percentage impedance | % | N/A
5 | Temperature rise (at 1800m)
Conditions:
| I: Passage of maximum continuous neutral current | A | 140
| II: Passage of rated current of auxiliary transformer | A | N/A
| III: Passage of nominal short time current for 10s | A | 2000
5.1 | Top oil temperature rise for condition:
| a) I | k | 55
| b) II | k | N/A
| c) III | k | 55
| d) I and II | k | N/A
| e) I and III | k | 55
5.2 | NEC winding temperature rise (max_calculated) for condition:
| a) I | k | 60
| b) II | k | N/A
| c) III | k | 150
| d) I and II | k | N/A
| e) I and III | k | 150
5.3 | Maximum NER temperature (measured) for Metallic NER under any condition: | oC | N/A
6 | Material
| a) NEC winding |  | Cu
| b) AUX HV winding |  | N/A
| c) AUX LV winding |  | N/A
| d) Grade of NER elements |  | N/A
7 | Material thickness
| a) Tank top | mm | xxxxxxxxxx
| b) Tank bottom | mm | xxxxxxxxxx
| c) Tank sides | mm | xxxxxxxxxx
| d) Conservator | mm | xxxxxxxxxx
| e) Radiator tubes (if any) | mm | xxxxxxxxxx
8 | Housing and corrosion protection
| a) Material - Coastal |  | xxxxxxxxxx
| b) Corrosion protection - Coastal |  | As 240-56030674
| c) Tank colour |  | Cloud Grey
| d) Conservator colour |  | White
9 | Minimum insulation for windings
(Note - Provide detailed test plan for evaluation)
9.1 | Impulse withstand test voltage for line terminal:
| Primary | kV | 75
9.2 | Sixty-second, separate source
| Primary | kV | 20
9.3 | Sixty-second, induced-overvoltage withstand test voltages
| Primary to earth | kV | 13.2
9.4 | Inter-turn winding insulation
| Paper/ Enamel |  | xxxxxxxxxx
| Enamel grade |  | Grade 3 or Better
| Paper thickness |  | xxxxxxxxxx
9.5 | Inter-turn winding insulation
| a) Highest inter-layer stress in non tap part of winding | kV | <5kV/mm
| b) Highest inter-layer stress in tap part of winding | kV | <5kV/mm
10 | HV Bushings - General |  | 33kV solid bushing that conform to IEC 60815
a) Profile characteristics - Coastal
| b) Minimum creepage - Coastal | mm/kV | 31
| c) Material - Coastal |  | xxxxxxxxxx
| d) Manufacturer and type - Coastal |  | xxxxxxxxxx
10.1 | HV Bushings – Details
| a) Type |  | Outdoor
| b) Manufacturer, Model and Type |  | xxxxxxxxxx
| c) Stem Size (diameter x length) | mm | 26 x 125
| d) Current Rating including 20% overload | A | xxxxxxxxxx
| e) Impulse Withstand Voltage at Sea Level | kV | 200
| f) Power Frequency Withstand Voltage | kV | 70
| g) Creepage | mm/kV | 31
| h) Protected Creepage | mm | xxxxxxxxxx
10.2 | Neutral Bushings – Detail
| a) Type |  | Outdoor
| b) Manufacturer, Model and Type |  | xxxxxxxxxx
| c) Stem Size (diameter x length) | mm | 26 x 125
| d) Current Rating including 20% overload | A | xxxxxxxxxx
| e) Impulse Withstand Voltage at Sea Level | kV | xxxxxxxxxx
| f) Power Frequency Withstand Voltage | kV | xxxxxxxxxx
| g) Creepage | mm/kV | 31
| h) Protected Creepage | mm | xxxxxxxxxx
11 | Electrical Test Requirements
| Temperature rise tests on one unit (Type) |  | YES, TYPE
| Lightning Impulse test |  | YES, ROUTINE
| Short Duration Induced overvoltage test (no PD measurment) |  | YES, ROUTINE
| Separate source over-voltage withstand test |  | YES, ROUTINE
| Short-circuit withstand tests |  | YES TYPE AND PLEASE PROVIDE CALCULATIONS TO PROVE SHORT CIRCUIT CAPABILITY
| Insulation resistance |  | YES, ROUTINE
| Winding Resistance |  | YES, ROUTINE
| Ratio test |  | YES, ROUTINE
| Impedance tests |  | YES, ROUTINE
| Pressure tightness tests |  | YES, ROUTINE
| Load and No-Load losses |  | YES, ROUTINE
| Measurement of zero sequence impedance. |  | YES, ROUTINE
| Short–time current test on NEC/NER |  | YES, TYPE
| Vacuum test |  | YES, ROUTINE
| Dye penetrant test on all welds |  | YES, ROUTINE
12 | Current Transformers
12.1 | REF and Differential
| a) Manufacturer |  | xxxxxxxxxx
| b) Ratio |  | 2400/1
| c) Accuracy Class (on 600/1 ratio) |  | TPS
| d) Max Excitation Current at 300V | mA | 100
| e) Max Internal Resistance on 600/1 Ratio | Ω | 2.4
| f) Secondary Voltage/Turn | V/turn | 0.5
| g) Secondary Internal resistance/Turn | mΩ/turn | 4
| h) Location |  | xxxxxxxxxx
| i) Reference Number for the Mag. Curve |  | xxxxxxxxxx
12.2 | IDMTEF
| a) Manufacturer |  | xxxxxxxxxx
| b) Ratio |  | 100/1
| c) Accuracy Class (on 600/1 ratio) |  | 10P10
| d) Location ( Earthed End of NER near Resistor) |  | xxxxxxxxxx
| e) Reference Number for the Mag. Curve |  | xxxxxxxxxx
13 | NER elements
| a) Manufacturer |  | N/A
| b) Type designation |  | N/A
| c) Number of elements |  | N/A
14 | Indicating and Protective Devices
14.1 | Buchholz relay |  | Comply to 240-56063908
| a) Manufacturer |  | xxxxxxxxxx
| b) Product Type Number |  | xxxxxxxxxx
| c) Minimum size | mm | 50
14.2 | Oil Temperature thermometer |  | Comply to 240-56063843
| a) Manufacturer |  | xxxxxxxxxx
| b) Product Type Number |  | xxxxxxxxxx
14.3 | Winding Temperature thermometer |  | Comply to 240-56063843
| a) Manufacturer |  | xxxxxxxxxx
| b) Product Type Number |  | xxxxxxxxxx
14.4 | Dehydrating Breathing |  | Comply to 240-56063886
| a) Manufacturer |  | xxxxxxxxxx
| b) Product Type Number |  | xxxxxxxxxx
14.5 | Oil Level Indicator |  | Comply to 240-56063843
| a) Manufacturer |  | xxxxxxxxxx
| b) Product Type Number |  | xxxxxxxxxx
15 | Overall dimensions
| a) NEC Height (Base of NEC to top of Conservator) | mm | 3000mm Max
| b) NEC + Stand Height | mm | xxxxxxxxxx
| c) Length | mm | xxxxxxxxxx
| d) Width | mm | xxxxxxxxxx
16 | Mass
| a) NEC core and winding | kg | xxxxxxxxxx
| b) NER | kg | N/A
| c) AUX core and winding | kg | N/A
| d) Tank and fittings | kg | xxxxxxxxxx
| e) Oil | kg | xxxxxxxxxx
| f) Total | Ton | 5 max
17 | Documentation
Provide references for:
| a) Outline drawings |  | xxxxxxxxxx
| b) Rating and diagram plate |  | xxxxxxxxxx
| c) Internal general assembly drawing |  | xxxxxxxxxx
| d) AUX transformer wiring diagram |  | N/A
17.1 | Please provide the test reports for the following electrical tests : |  | xxxxxxxxxx
| a) Power-frequency voltage withstand test. |  | xxxxxxxxxx
| b) Impulse test. |  | xxxxxxxxxx
| c) Separate source voltage withstand test. |  | xxxxxxxxxx
| d) Induced over voltage test. |  | xxxxxxxxxx
| e) Measurement of zero sequence impedance. |  | xxxxxxxxxx
| f) Temperature rise test. |  | xxxxxxxxxx
| g) Short-circuit test on AUX |  | N/A
| h) Short-time current test on NEC |  | xxxxxxxxxx
| i) Vacuum test |  | xxxxxxxxxx
| j) Accelerated Ageing Test for Composite Bushings |  | xxxxxxxxxx

## Deviation Schedule
Deviation schedule: A and B for 6.6 kV NECRT, 360A for 10s and 10A continuous
According to Specification : 240-57648848
Any deviations offered to this specification shall be listed below with reasons for deviation. In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective than that specified by Eskom.
1 | 2
Item | Proposed deviation

## Design Schedule
Annex A- Design schedules A and B for 6.6 kV NECRT, 360A for 10s and 10A continuous
Eskom Material Number: 0182735
Schedule A: Purchaser's specific requirements
Schedule B: Guarantees and technical particulars of equipment offered
According to Specification : 240-57648848
1 | 2 | 3 | 4 | 5 | 6
Item |  |  |  | Schedule A | Schedule B
1 | Core Steel
1.1 | Manufacturer of core steel |  |  | xxxxxxxxxx
1.2 | Grade of core steel |  |  | xxxxxxxxxx
1.3 | Thickness of core steel |  | mm | xxxxxxxxxx
2 | Aux Trfr Core dimensions
2.1 | Window height | [Aux WH] | mm | xxxxxxxxxx
2.2 | Distance between core limb centres | [Aux CL] | mm | xxxxxxxxxx
2.3 | Core Diameter | [Aux D] | mm | xxxxxxxxxx
2.4 | Filling Factor |  |  | xxxxxxxxxx
3 | NEC Core dimensions
3.1 | Window height | [NEC WH] | mm | xxxxxxxxxx
3.2 | Distance between core limb centres | [NEC CL] | mm | xxxxxxxxxx
3.3 | Core Diameter | [NEC D] | mm | xxxxxxxxxx
3.4 | Filling Factor |  |  | xxxxxxxxxx
4 | Cross sectional areas
4.1 | Wound limbs |  | mm2 | xxxxxxxxxx
4.2 | Yoke |  | mm2 | xxxxxxxxxx
5 | Total core masses | aux | kg | xxxxxxxxxx
|  | nec | kg | xxxxxxxxxx
6 | The design flux density at Un for:
6.1 | Wound limbs |  | T | xxxxxxxxxx
6.2 | Yoke |  | T | xxxxxxxxxx
7 | Volts/turn at the above flux densities |  | V/turn | xxxxxxxxxx
NEC CORE
8 | Winding design
8.1 | Winding arrangement (CORE / LV / HV ) |  |  | xxxxxxxxxx
8.2 | Conductor Yield strength |  | N/mm2 | xxxxxxxxxx
8.3 | Aux Winding 1 |  |  | LV
8.3.1 | Type (i.e. multilayer helix) |  |  | xxxxxxxxxx
8.3.2 | Lead type (End Fed / Centre Fed) |  |  | xxxxxxxxxx
8.3.3 | Number of turns |  |  | xxxxxxxxxx
8.3.4 | Inner Diameter |  | mm | xxxxxxxxxx
8.3.5 | Outer Diameter |  | mm | xxxxxxxxxx
8.3.6 | Radial build |  | mm | xxxxxxxxxx
8.3.7 | Magnetic height |  | mm | xxxxxxxxxx
8.3.8 | Conductor configuration |  |  | xxxxxxxxxx
8.3.9 | - Size |  |  | xxxxxxxxxx
8.3.10 | - Number |  |  | xxxxxxxxxx
8.3.11 | Conductor insulation |  | mm | xxxxxxxxxx
8.3.12 | Current density | A/mm2 |  | xxxxxxxxxx
8.3.13 | Temperature gradient winding – oil |  | °C (K) | xxxxxxxxxx
8.3.14 | Total conductor mass |  | kg | xxxxxxxxxx
8.4 | Aux Winding 2 |  |  | HV
8.4.1 | Type (i.e. multilayer helix) |  |  | xxxxxxxxxx
8.4.2 | Lead type (End Fed / Centre Fed) |  |  | xxxxxxxxxx
8.4.3 | Number of turns |  |  | xxxxxxxxxx
8.4.4 | Inner Diameter |  | mm | xxxxxxxxxx
8.4.5 | Outer Diameter |  | mm | xxxxxxxxxx
8.4.6 | Radial build |  | mm | xxxxxxxxxx
8.4.7 | Magnetic height |  | mm | xxxxxxxxxx
8.4.8 | Conductor configuration |  |  | xxxxxxxxxx
8.4.9 | - Size |  |  | xxxxxxxxxx
8.4.10 | - Number |  |  | xxxxxxxxxx
8.4.11 | Conductor insulation |  | mm | xxxxxxxxxx
8.4.12 | Current density | A/mm2 |  | xxxxxxxxxx
8.4.13 | Temperature gradient winding – oil |  | °C (K) | xxxxxxxxxx
8.4.14 | Total conductor mass |  | kg | xxxxxxxxxx
8.5 | NEC Winding
8.5.1 | Type (i.e. multilayer helix) |  |  | xxxxxxxxxx
8.5.2 | Lead type (End Fed / Centre Fed) |  |  | xxxxxxxxxx
8.5.3 | Number of turns |  |  | xxxxxxxxxx
8.5.4 | Inner Diameter |  | mm | xxxxxxxxxx
8.5.5 | Outer Diameter |  | mm | xxxxxxxxxx
8.5.6 | Radial build |  | mm | xxxxxxxxxx
8.5.7 | Magnetic height |  | mm | xxxxxxxxxx
8.5.8 | Conductor configuration |  |  | xxxxxxxxxx
8.5.9 | - Size |  |  | xxxxxxxxxx
8.5.10 | - Number |  |  | xxxxxxxxxx
8.5.11 | Conductor insulation |  | mm | xxxxxxxxxx
8.5.12 | Current density | A/mm2 |  | xxxxxxxxxx
8.5.13 | Temperature gradient winding – oil |  | °C (K) | xxxxxxxxxx
8.5.14 | Total conductor mass |  | kg | xxxxxxxxxx
9 | NER elements
9.1 | a) Manufacturer |  |  | NA
9.2 | b) Type designation |  |  | NA
9.3 | c) Number of elements |  |  | NA
9.4 | d) Resistance |  |  | NA
10 | Inter-winding Insulation
10.1 | CORE -NEC winding |  |  | xxxxxxxxxx
10.1.1 | Number of barriers |  |  | xxxxxxxxxx
10.1.2 | Barrier thickness |  | mm | xxxxxxxxxx
10.1.3 | Distance from windings |  | mm | xxxxxxxxxx
10.1.4 | Distance between barriers |  | mm | xxxxxxxxxx
10.2 | LV winding to HV winding |  |  | xxxxxxxxxx
10.2.1 | Number of barriers |  |  | xxxxxxxxxx
10.2.2 | Barrier thickness |  | mm | xxxxxxxxxx
10.2.3 | Distance from windings |  | mm | xxxxxxxxxx
10.2.4 | Distance between barriers |  | mm | xxxxxxxxxx
WH
CL
D

## Information Schedule
Annex A- Information schedules A and B for 6.6 kV NECRT, 360A for 10s and 10A continuous
Eskom Material Number: 0182735
Schedule A: Purchaser's specific requirements
Schedule B: Guarantees and technical particulars of equipment offered
According to Specification : 240-57648848
1 | 2 | 3 | 4 | 5
Item | Description |  | Schedule A | Schedule B
1 | Transformer general information
1.1 | Manufacturer |  | xxxxxxxxxx
1.2 | Place of manufacture |  | xxxxxxxxxx
2 | Oil quantities:
2.1 | Transformer tank | l | xxxxxxxxxx
2.2 | Tap-changer | l | xxxxxxxxxx
2.3 | Radiators | l | xxxxxxxxxx
2.4 | Conservator (Main & tap-changer) | l | xxxxxxxxxx
3 | Masses
3.1 | Mass of core steel | kg | xxxxxxxxxx
3.3 | Total dry insulation mass | kg | xxxxxxxxxx
3.4 | Total mass of active part | kg | xxxxxxxxxx
3.5 | Mass of tank and fittings | kg | xxxxxxxxxx
3.6 | Mass of coolers | kg | xxxxxxxxxx
3.7 | Mass of oil | kg | xxxxxxxxxx
3.8 | Greatest transportation mass | kg | xxxxxxxxxx
4 | Primary / Secondary zero sequence impedances
4.1 | On principal tapping | % | xxxxxxxxxx
4.2 | On extreme plus tapping | % | xxxxxxxxxx
4.3 | On extreme minus tapping | % | xxxxxxxxxx
5 | Primary / Neutral zero sequence impedances
5.1 | On principal tapping | % | xxxxxxxxxx
5.2 | On extreme plus tapping | % | xxxxxxxxxx
5.3 | On extreme minus tapping | % | xxxxxxxxxx
6 | Secondary / Neutral zero sequence impedances
6.1 | On principal tapping | % | xxxxxxxxxx
6.2 | On extreme plus tapping | % | xxxxxxxxxx
6.3 | On extreme minus tapping | % | xxxxxxxxxx
7 | Filling medium for transport |  | xxxxxxxxxx