## BOARD NAME
[14 empty] | Template Unique Identifier: |  | 240-77301384 (Rev 2)
[14 empty] | Document Unique Identifier: |  | XXX-XXXXXXXX
[6 empty] | ELECTRICAL LOW VOLTAGE LOAD SCHEDULE | [7 empty] | Revision No: |  | <x.x>
[14 empty] | Effective Date: |  | 2018-02-01
GENERATION PLANT ENGINEERING
| PRICE SCHEDULE | [12 empty] | PANEL FAULT CURRENT RATING |  |  | 50kA
| INCOMING CURRENT RATING |  |  | 2600A | [9 empty] | PEAK FAULT CURRENT RATING |  |  | 105kA
| VOLTAGE |  |  | 400V | [9 empty] | POWER FREQUENCY TEST |  |  | 2.5kV
| PHASES |  |  | 3 Phases | [9 empty] | RATED IMPULSE VOLTAGE |  |  | 8kV
PLANT CONDIFICATION |  | DESCRIPTION | LOAD RATING |  |  | PROPOSED SCPD |  | OFFERED SCPD |  | NUMBER OF POLES | CIRCUIT TYPE | I/O BLOCK DIAGRAM | STARTER PROTECTION CLASS | TYPICAL SCHEMATIC DIAGRAM REFERENCE | POWER CABLE DATA
CIRCUIT NUMBER | PROCESS KKS CODE | LABEL (< 60 Characters) | RATED (kW) | FULL LOAD CURRENT (Amps) | CALCULATED LOAD CURRENT (Amps) | CURRENT RATING | TYPE | CURRENT RATING | TYPE | [5 empty] | QUANTITY | CORES PER CABLE | CORE AREA
1 |  | UNIT # BRD INCOMER |  |  |  | 2500 | ACB | 2500 | ACB | 3 Phase 3 wire
2 |  | BUS-SECTION |  |  |  | 16 | MCB | 16 | MCB | 1 Phase 2 wire
3 |  | CONTROL SUPPLY
4 |  | Lub Oil Pump | 37 | 75 | 68 | 100 | MCCB | 100 | MCCB | 3 Phase 3 wire
5 |  | Solenoid Valve |  |  | 6 | 10 | MCB | 10 | MCB | 1 Phase 2 wire
|  | TOTAL CALCULATED CURRENT (A) |  |  | 74
| MCB's GROUP | MCB's GROUP CIRCUITS | SCPD TYPE | IO Block
| GROUP 1 | Circuits 2,4,74,76,78, | CFS
REVISION HISTORY
[14 empty] | KKS Code | 1 0BFB
[9 empty] | REVISION NO | DESCRIPTION OF REVISION |  | DATE |  | System | LOW VOLTAGE SWITCHGEAR
[9 empty] | 0 | First issue |  |  |  | Function | UNIT 1 380V UNIT LIGHTING BOARD 1 ESS
[14 empty] | Type | LOAD SCHEDULE
Eskom No.
[14 empty] | Date |  | Compiled by
[14 empty] | Date |  | Checked by
[14 empty] | Date |  | Approved by
[14 empty] | Drawing No. |  | Rev No. | 0

## NOTES
Item | Description
Circuit Number | This refers to Circuit number as a reference number that will be used on Switchgear Schedule
SCPD | Short Circuit Protection Device
3 Phase 3 wire | 3 Phases without Neutral (3 Poles SCPD)
3 Phase 4 wire | 4 Phases + Neutral (3 Poles SCPD)
1 Phase 2 wire | Single Phase + Neutral (2 Poles SCPD)
1 Phase 1 wire | Single Phase without Neutral (1 Pole SCPD)
ACB | Air Circuit Breaker
MCCB | Moulded Case Circuit Breaker
CFS | Combine Fuse Switch (Fuse Switch Disconnector)
MCB | Maniature Circuit Breaker
Circuit Type | INC - INCOMER
FDR - FEEDER
DOL < 11kW - Direct On Line Starter below 11kW
DOL ≥ 11kW - Direct On Line Starter equal and greater than 11kW
DOLR < 11kW - Forward Reverse Starter above 11kW
I/O Block Diagram | Input Output Block Diagram reference from C&I
Starter Protection Class (Tripping Class) | Tripping class of thermal overload release defines the maximum tripping time starting from cold. This time refers to a symmetrical load on 3 poles at 7.2 times the set current (e.g. Class 10 classifies the value for the maximum permissible tripping time in seconds). Tripping time will be 10, 20, 30 seconds for Class 10, 20, 30, respectively
TOTAL CALCULATED CURRENT | This is the total calculated current whereby by Diversity and Utilasation factors have been take into account