NEC3 Engineering & Construction Contract

| Between | ESKOM HOLDINGS SOC LIMITED (Reg No. 2002/015527/30) |  |
| --- | --- | --- |
| and | (Reg No. __________________________ ) |  |
| for | Supply, Installation and Commissioning of Control Kiosks Fire Detection System Project at Hydra Substation. |  |
| Contents: |  | No of pages |
| Part C1 | Agreements & Contract Data | [●] |
| Part C2 | Pricing Data | [●] |
| Part C3 | Scope of Work | [●] |
| Part C4 | Site Information | [●] |
| CONTRACT No. |  |  |

Part C1: Agreements & Contract Data

| Contents: |  | No of pages |
| --- | --- | --- |
| C1.1 | Form of Offer and Acceptance [to be inserted from Returnable Documents at award stage] | [●] |
| C1.2a | Contract Data provided by the Employer | [●] |
| C1.2b | Contract Data provided by the Contractor [to be inserted from Returnable Documents at award stage] | [●] |
| C1.3 | Proforma Guarantees | [●] |

C1.1 Form of Offer & Acceptance

## Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Supply, Installation and Commissioning of Control Kiosks Fire Detection System Project at Hydra Substation.

The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data.

Delete the row for the Options which do not apply

| Options A | The offered total of the Prices exclusive of VAT is | R |
| --- | --- | --- |
|  | Value Added Tax @ 15% is | R |
|  | The offered total of the amount due inclusive of VAT is | R |
|  | (in words) |  |

This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| For the tenderer: |  |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |
| Tenderer’s CIDB registration number: |  |  |  |  |

## Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in:

Part C1		Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2		Pricing Data

Part C3		Scope of Work: Works Information

Part C4		Site Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed original copy of this document, including the Schedule of Deviations (if any).

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| for the Employer |  |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |

Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

## Schedule of Deviations to be completed by the Employer prior to contract award

Note:

- This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.

- The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

- A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

| No. | Subject | Details |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |
| 7 |  |  |

By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement.

|  | #### For the tenderer: |  | #### For the Employer |
| --- | --- | --- | --- |
| Signature |  |  |  |
| Name |  |  |  |
| Capacity |  |  |  |
| On behalf of | (Insert name and address of organisation) |  | (Insert name and address of organisation) |
| Name & signature of witness |  |  |  |
| Date |  |  |  |

C1.2 ECC3 Contract Data

# Part one - Data provided by the Employer

| ## Clause | ## Statement | ## Data |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | ## General |  |  |  |  |
|  | The conditions of contract are the core clauses and the clauses for main Option |  |  |  |  |
|  |  | A: Priced contract with activity schedule |  |  |  |
|  | dispute resolution Option | W1: Dispute resolution procedure |  |  |  |
|  | and secondary Options |  |  |  |  |
|  |  | X2 Changes in the law |  |  |  |
|  |  | X7: Delay damages X13: Performance Bond |  |  |  |
|  |  | X15: Limitation of Contractor’s liability for design to reasonable skill and care |  |  |  |
|  |  | X16: Retention |  |  |  |
|  | [always used by Eskom] | X18: Limitation of liability |  |  |  |
|  |  | Z: Additional conditions of contract |  |  |  |
|  | of the NEC3 Engineering and Construction Contract, June 2005 (ECC3) (with amendments June 2006) |  |  |  |  |
| 10.1 | The Employer is (Name): | Eskom Holdings Limited (reg no: 2002/015527/30), a juristic person incorporated in terms of the company laws of the Republic of South Africa |  |  |  |
|  | Address | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |  |  |
| 10.1 | The Project Manager is: (Name) | Nthuseng Dlamini |  |  |  |
|  | Address | 1 Maxwell drive, Sunninghill, 0001 |  |  |  |
|  | Tel e-mail | +27 (0) 11 800 4958/ 082 459 2098 Dlamincn@eskom.co.za |  |  |  |
| 10.1 | The Supervisor is: (Name) | To be advised |  |  |  |
|  | Tel No. |  |  |  |  |
|  | e-mail |  |  |  |  |
| 11.2(13) | The works are | - Supply, Install and commission of Control Kiosks Fire Detection System in Transmission Substation. - Issuing of certificate of compliance - Supply of all operational manuals and maintenance manuals - Training of Employer personnel |  |  |  |
| 11.2(14) | The following matters will be included in the Risk Register | - Control Kiosks Fire Detection System electrical contract. The contractor is to ensure compliance to all SHEQ requirements. - Material suppliers. The contractor needs to ensure that suppliers are identified and no delays are experienced as a result of distances to be covered by suppliers. - Theft. The site and working areas are to be guarded to ensure that no theft can take place that will affect the continuity of supply or loss to the employer’s existing assets. - Labour issues. These issues are to be properly managed in the event that local labour is to be hired to limit any disruptions of the work by local residents. - Health care facilities. The contractor is to note where the nearest health care facilities are and the response time of emergency medical rescue service providers in case of an emergency. - Weather. Abnormally extremely hot and humid weather in and windy temperatures may be experienced during summer season; and summer. The contractor needs to take precautions when planning the sequence and resources for the works. |  |  |  |
| 11.2(15) | The boundaries of the site are | Perimeter of Hydra substation |  |  |  |
| 11.2(16) | The Site Information is in | Part 4: Site Information |  |  |  |
| 11.2(19) | The Works Information is in | Part 3: Scope of Work and all documents and drawings to which it makes reference. |  |  |  |
| 12.2 | The law of the contract is the law of | the Republic of South Africa |  |  |  |
| 13.1 | The language of this contract is | English |  |  |  |
| 13.3 | The period for reply is | Two (2) weeks |  |  |  |
| ## 2 | ## The Contractor's main responsibilities | Data required by this section of the core clauses is provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data. |  |  |  |
| ## 3 | ## Time |  |  |  |  |
| 11.2(3) | The completion date for the whole of the works is | 30 July 2022 |  |  |  |
| 11.2(9) | The key dates and the conditions to be met are: | Condition to be met |  |  | key date |
|  |  | 1 | Supply the equipment to Eskom for approval |  | 01 June 2022 |
|  |  | 2 | Installation completed |  | 30 July 2022 |
|  |  | 3 | Issue compliance certificates and handover to Eskom |  | 30 July 2022 |
| 30.1 | The access dates are: |  |  |  |  |
|  |  |  | The Supplier shall request access to the Employer’s site, from the Project Manager, at least two weeks prior to access being required. Access to site shall be granted at any time during the calendar days. Access to site may be granted at other times, on request, at the Project Manager’s sole discretion. |  |  |
| 31.1 | The Contractor is to submit a first programme for acceptance within | Within 1 week of the Contract Date. |  |  |  |
| 31.2 | The starting date is | 01 July 2022 |  |  |  |
| 32.2 | The Contractor submits revised programmes at intervals no longer than | 2 weeks. |  |  |  |
| 35.1 | The Employer is not willing to take over the works before the Completion Date. |  |  |  |  |
| ## 4 | ## Testing and Defects |  |  |  |  |
| 42.2 | The defects date is | 52 weeks after Completion of the whole of the works. |  |  |  |
| 43.2 | The defect correction period is | 2 weeks |  |  |  |
| ## 5 | ## Payment |  |  |  |  |
| 50.1 | The assessment interval is | between the 25th day of each successive month. |  |  |  |
| 51.1 | The currency of this contract is the | South African Rand. |  |  |  |
| 51.2 | The period within which payments are made is | 14 days after receipt of a valid invoice |  |  |  |
| 51.4 | The interest rate is | (i) zero percent above the publicly quoted prime rate of interest (calculated on a 365 day year) charged from time to time by the Standard Bank of South Africa (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and (ii) the LIBOR rate applicable at the time for amounts due in other currencies. LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove. |  |  |  |
| ## 6 | ## Compensation events |  |  |  |  |
| 60.1(13) | The place where weather is to be recorded is: | De Aar, Hydra Substation, Northern Cape Province |  |  |  |
|  | The weather measurements to be recorded for each calendar month are, | the cumulative rainfall (mm) |  |  |  |
|  |  | the number of days with rainfall more than 10 mm |  |  |  |
|  |  | the number of days with minimum air temperature less than 0 degrees Celsius |  |  |  |
|  |  | the number of days with snow lying at 09:00 hours South African Time |  |  |  |
|  |  | and these measurements: |  |  |  |
|  | The weather measurements are supplied by | The South African Weather Bureau |  |  |  |
|  | The weather data are the records of past weather measurements for each calendar month which were recorded at: | Substation referred in the scope of works |  |  |  |
|  | and which are available from: | the South African Weather Bureau and included in Annexure A to this Contract Data provided by the Employer |  |  |  |
| ## 7 | ## Title | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data. |  |  |  |

| ## 8 |  | ## Risks and insurance |  |
| --- | --- | --- | --- |
| 80.1 |  | These are additional Employer's risks |  |
| 84.1 |  | The Employer provides these insurances from the Insurance Table | as stated for “Format A available on http://www.eskom.co.za/live/content.php?Item_ID=9248 (See Annexure B for basic guidance) |
| 84.2 |  | The minimum limit of indemnity for insurance in respect of loss of or damage to property (except the works, Plant, Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) caused by activity in connection with this contract for any one event is | whatever the Contractor deems necessary in addition to that provided by the Employer. |
| 84.2 |  | The minimum limit of indemnity for insurance in respect of death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract for any one event is | As prescribed by the Compensation for Occupational Injuries and Diseases Act No. 130 of 1993 and the Contractor’s common law liability for people falling outside the scope of the Act with a limit of Indemnity of not less than R500 000 (Five hundred thousand Rands). |
| ## 9 |  | ## Termination | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data. |
| ## 10 |  | ## Data for main Option clause |  |
| A |  | Priced contract with activity schedule | There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data. |
| ## 11 |  | ## Data for Option W1 |  |
| W1.1 |  | The Adjudicator is (Name) | the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him. (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA). |
| W1.2(3) |  | The Adjudicator nominating body is: | the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the London Institution of Civil Engineers. (See www.ice-sa.org.za ) or its successor body. |
| W1.4(2) |  | The tribunal is: | arbitration. |
| W1.4(5) |  | The arbitration procedure is | the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body. |
|  |  | The place where arbitration is to be held is | Johannesburg, South Africa |
|  |  | The person or organisation who will choose an arbitrator - if the Parties cannot agree a choice or - if the arbitration procedure does not state who selects an arbitrator, is | the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body. |
| ## 12 |  | ## Data for secondary Option clauses |  |
| X2 |  | Changes in the law | There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data. |
| X4 |  | Parent company guarantee | There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data. |
| X7 |  | Delay damages (but not if Option X5 is also used) |  |
| X7.1 |  | Delay damages for Completion of the whole of the works are | 0.1% per day up to a limit of 15% of total contract value |
| X13 |  | Performance bond |  |
| X13.1 |  | The amount of the performance bond is | Equivalent to the contract value (excl. VAT) per the Form of Offer and Acceptance |
| X15 |  | Limitation of the Contractor’s liability for his design to reasonable skill & care | There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data. |
| X16 |  | Retention (not used with Option F) |  |
| X16.1 |  | The retention free amount is | R0. |
|  |  | The retention percentage is | 5% of every invoice (excl. VAT) per the Form of Offer and Acceptance |
| X18 |  | Limitation of liability |  |
| X18.1 |  | The Contractor’s liability to the Employer for indirect or consequential loss is limited to: | R0.0 (zero Rand) |
| X18.2 |  | For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to: | the amount of the deductibles relevant to the event described in the insurance policy format selected in the data for clause 84.1 above, which policy is available on http://www.eskom.co.za/live/content.php?Item_ID=9248 |
| X18.3 |  | The Contractor’s liability for Defects due to his design which are not listed on the Defects Certificate is limited to | The greater of - the total of the Prices at the Contract Date and - the amounts excluded and unrecoverable from the Employer’s assets policy for correcting the Defect (other than the resulting physical damage which is not excluded) plus R15M first amount payable in terms of the Employer’s assets policy. |
| X18.4 |  | The Contractor’s total liability to the Employer for all matters arising under or in connection with this contract, other than excluded matters, is limited to: | the total of the Prices other than for the additional excluded matters. The Contractor’s total liability for the additional excluded matters is not limited. The additional excluded matters are amounts for which the Contractor is liable under this contract for - Defects due to his design which arise before the Defects Certificate is issued, - Defects due to manufacture and fabrication outside the Site, - loss of or damage to property (other than the works, Plant and Materials), - death of or injury to a person and - infringement of an intellectual property right. |
| X18.5 |  | The end of liability date is | (i) seven years after the defects date for latent Defects and (ii) the date on which the liability in question prescribes in accordance with the Prescription Act No. 68 of 1969 (as amended or in terms of any replacement legislation) for any other matter. A latent Defect is a Defect which would not have been discovered on reasonable inspection by the Employer or the Supervisor before the defects date, without requiring any inspection not ordinarily carried out by the Employer or the Supervisor during that period. If the Employer or the Supervisor do undertake any inspection over and above the reasonable inspection, this does not place a greater responsibility on the Employer or the Supervisor to have discovered the Defect. |
| Z |  | The Additional conditions of contract are | Z1 to Z12 always apply. |
| Z1 | Cession delegation and assignment |  |  |
| Z1.1 | The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer. |  |  |
| Z1.2 | Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry and the Electricity Distribution Industry. |  |  |
| Z2 | Joint ventures |  |  |
| Z2.1 | If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract. |  |  |
| Z2.2 | Unless already notified to the Employer, the persons or organisations notify the Project Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf. |  |  |
| Z2.3 | The Contractor does not substantially alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing. |  |  |
| Z3 |  | Change of Broad Based Black Economic Empowerment (B-BBEE) status |  |
| Z3.1 |  | Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change. |  |
| Z3.2 |  | The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Project Manager within thirty days of the notification or as otherwise instructed by the Project Manager. |  |
| Z3.3 |  | Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Works. |  |
| Z3.4 |  | Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P3 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93. |  |
| Z4 | Ethics |  |  |
| Z4.1 | Any offer, payment, consideration, or benefit of any kind made by the Contractor, which constitutes or could be construed either directly or indirectly as an illegal or corrupt practice, as an inducement or reward for the award or in execution of this contract constitutes grounds for terminating the Contractor’s obligation to Provide the Works or taking any other action as appropriate against the Contractor (including civil or criminal action). |  |  |
| Z4.2 | The Employer may terminate the Contractor’s obligation to Provide the Works if the Contractor (or any member of the Contractor where the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations) is found guilty by a competent court, administrative or regulatory body of participating in illegal or corrupt practices. Such practices include making of offers, payments, considerations, or benefits of any kind or otherwise, whether in connection with any procurement process or contract with the Employer or other people or organisations and including in circumstances where the Contractor or any such member is removed from the an approved vendor data base of the Employer as a consequence of such practice. |  |  |
| Z4.3 | Notwithstanding the provisions of core clause 90.2, the procedures on termination in terms of this clause are P1, P2 and P3 as stated in the core clause 92 and the amount due is A1 and A3 as stated in core clause 93. |  |  |
| Z5 | Confidentiality |  |  |
| Z5.1 | The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time). Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient. |  |  |
| Z5.2 | If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Project Manager. |  |  |
| Z5.3 | In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure. In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed. |  |  |
| Z5.4 | The taking of images (whether photographs, video footage or otherwise) of the works or any portion thereof, in the course of Providing the Works and after Completion, requires the prior written consent of the Project Manager. All rights in and to all such images vests exclusively in the Employer. |  |  |
| Z5.5 | The Contractor ensures that all his subcontractors abide by the undertakings in this clause. |  |  |
| Z6 | Waiver and estoppel: Add to core clause 12.3: |  |  |
| Z6.1 | Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Project Manager, the Supervisor, or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing. |  |  |
| Z7 |  | Health, safety and the environment: Add to core clause 27.4 |  |
| Z7.1 |  | The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the works. Without limitation the Contractor: - accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2003 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Site; - warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of works; and - undertakes, in and about the execution of the works, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |
| Z7.2 |  | The Contractor, in and about the execution of the works, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |
| Z8 | Provision of a Tax Invoice and interest. Add to core clause 51 |  |  |
| Z8.1 | Within one week of receiving a payment certificate from the Project Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Works Information, showing the amount due for payment equal to that stated in the payment certificate. |  |  |
| Z8.2 | If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice. Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made. |  |  |
| Z8.3 | The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment. |  |  |
| Z9 | Notifying compensation events |  |  |
| Z9.1 | Delete from the last sentence in core clause 61.3, “unless the Project Manager should have notified the event to the Contractor but did not”. |  |  |
| Z10 | Employer’s limitation of liability |  |  |
| Z10.1 | The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand) |  |  |
| Z10.2 | The Contractor’s entitlement under the indemnity in 83.1 is provided for in 60.1(14) and the Employer’s liability under the indemnity is limited to compensation as provided for under the compensation events stated in this contract. |  |  |
| Z11 | Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it": |  |  |
| Z11.1 | or had a judicial management order granted against it. |  |  |
| Z12 | Addition to secondary Option X7 Delay damages (if applicable in this contract) |  |  |
| Z12.1 | If the amount due for the Contractor’s payment of delay damages reaches the limits stated in this Contract Data for Option X7 or Options X5 and X7 used together, the Employer may terminate the Contractor’s obligation to Provide the Works using the same procedures and payment on termination as those applied for reasons R1 to R15 or R18 stated in the Termination Table. |  |  |
| Z13 | Supplier Development and Localisation ( SD&L) |  |  |
| Z15.1 | The Contractor undertakes to achieve the SD&L targets per Annexure C attached hereto. |  |  |
| Z15.2 | 2.5% SD&L retention for non-compliance to SD&L obligations (excl. VAT) per the Form of Offer and Acceptance, as security for the fulfilment by the Contractor of his SD&L undertakings. Quarterly monitoring and reporting as per SD &L targets. |  |  |
| Z15.3 | If the Contractor has at Completion achieved its local content, skills development and job creation targets, the guarantee will be returned to the Contractor. |  |  |
| Z15.4 | If the Contractor has at the end of the Contract only partially achieved his local content, skills development and job creation targets, the Contractor will be placed on terms to either pay the amount calculated as due, being in proportion to the extent to which the targets have been achieved, expressed as a percentage of achievement versus target, or make good on the targets, within 4 weeks of the date of dispatch of the notice to either pay or make good. Should the Contractor not have complied by that time, the SD&L retention will be called for such amounts. |  |  |
| Z15.5 Z15.6 | If the Contractor has at the end of the contract not achieved any one or more of the local content, skills development and job creation targets, the Contractor will be placed on terms to either pay the amount calculated as due, or make good on the targets, within 4 weeks of the date of dispatch of the notice to either pay or make good. Should the Contractor not have complied by that time, the SD&L retention will be called for such amounts. The parties agree that any amounts forfeited by the Contractor for the non-achievement of his SD&L targets, is a reasonable estimate of the potential loss suffered by the Employer due to the Contractor’s failure to achieve the targets as set, and is a reasonable penalty in the circumstances |  |  |

# Annexure A:	 One-in-ten-year-return weather data obtained from SA Weather Bureau for [De Aar station]

If any one of these weather measurements recorded within a calendar month, before the Completion Date for the whole of the works and at the place stated in this Contract Data is shown to be more adverse than the amount stated below then the Contractor may notify a compensation event.

|  | Weather measurement |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Month | Cumulative rainfall (mm) | Number of days with rain more than 10mm | Number of days with min air temp < 0 deg.C | Number of days with snow lying at 08:00 CAT | [Other measurements if applicable] |
| January | [●] | [●] | [●] | [●] |  |
| February | [●] | [●] | [●] | [●] |  |
| March | [●] | [●] | [●] | [●] |  |
| April | [●] | [●] | [●] | [●] |  |
| May | [●] | [●] | [●] | [●] |  |
| June | [●] | [●] | [●] | [●] |  |
| July | [●] | [●] | [●] | [●] |  |
| August | [●] | [●] | [●] | [●] |  |
| September | [●] | [●] | [●] | [●] |  |
| October | [●] | [●] | [●] | [●] |  |
| November | [●] | [●] | [●] | [●] |  |
| December | [●] | [●] | [●] | [●] |  |

Only the difference between the more adverse recorded weather and the equivalent measurement given above is taken into account in assessing a compensation event.

# Annexure B:	Insurance provided by the Employer

These notes are provided as guidance to tendering contractors and the Contractor about the insurance provided by the Employer. Details of the insurance itself are available from the internet web link given below.

- For the purpose of works contracts, insurance provided by Eskom (the Employer) has been arranged on the basis of “project” or “contract” value, where the value is the total of the Prices at Completion of the whole of the works including VAT.

A “project” is a collection of contracts or work packages to be undertaken as part of a single identified capital expansion or refurbishment of a particular asset or facility.

A “contract” is a single contract not linked to or being part of a “project”.

- For ECC3 there are three main “formats” of cover and deductible structure; Format A, Format B and Format Dx.

Format A is for a project or contract value less than or equal to R350M (three hundred and fifty million Rand) inclusive of VAT.

Format B is for a project or contract value greater than R350M .(three hundred and fifty million Rand) inclusive of VAT.

In the case of contracts / packages within a project:

- For a contract / package of R50M which is part of a R400M project, Format B will apply

- For a contract / package of R250M which is part of a R6 billion project, Format B will apply;

- For a contract / package of R120M which is part of a R350M project Format A will apply;

For a contract which is not part of a project the same limits apply:

- For a contract of R50M, Format A will apply

- For a contract of R355M, Format B will apply.

Format Dx applies only to Distribution Division projects and contracts. If a Distribution Division project or contract exceeds the Format A limit, the Eskom Insurance Management Services [EIMS] need to be contacted for advice on how to formulate the insurance cover.  Cover and deductibles for Distribution Division are per the relevant policy available on the internet web link given below.

Format A generally applies to Transmission Division projects and contracts. If a Transmission Division project or contract exceeds the Format A limit, the Eskom Insurance Management Services [EIMS] need to be contacted for advice on how to formulate the insurance cover.

- Tendering contractors should note that cover provided by the Employer is only per the policies available on the internet web link listed below and may not be the cover required by the tendering contractor or as intended by each of the listed insurances in the left hand column of the Insurance Table in clause 84.2.  In terms of clause 84.1 “the Contractor provides the insurances stated in the Insurance Table except any insurance which the Employer is to provide”.  Hence the Contractor provides insurance which the Employer does not provide and in cases where the Employer does provide insurance the Contractor insures for the difference between what the Insurance Table requires and what the Employer provides.

- When the Marine Insurance is required the Contractor needs to obtain a copy of the latest edition of Eskom’s Marine Policies Procedures found at internet website given below.

- Further information and full details of all Eskom provided policies and procedures may be obtained from:

http://www.eskom.co.za/live/content.php?Item_ID=9248

Annexure C Supplier Development & Localisation (SD&L) targets

| TABLE 1: SUPPLIER DEVELOPMENT AND LOCALISATION COMPLIANCE MATRIX FOR SUPPLIERS AND CONTRACTOR |  |  |  |  |
| --- | --- | --- | --- | --- |
| Criteria | Weight (%) | Total Target (%) | Proposed Target (%) | Total Overall Weighted Score |
| Local Content to SA | 25% | 100% | 100% | 0.00% |
| Procurement from BWO | 25% | 20% | 2.5% | 0.00% |
| Procurement from BYO/BPLwD | 25% | 10% | 2.5% | 0.00% |
| Skills development | 25% |  |  | 0.00% |
| Total | 100% |  |  | 0.00% |
|  | Total Supplier Development and Localisation Score |  |  | 0.00% |

| TABLE 2: SKILLS DEVELOPMENT COMPLIANCE MATRIX |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Skill Type (Occupation) | Weight (%) | Target Number of Persons to be Trained (Local to South Africa) | Proposed Number of Persons to be Trained (Local to South Africa) | Target Number of Persons to be Trained (Local to Site) | Proposed Number of Persons to be Trained (Local to Site) | Total Weighted Score |
| Site Supervisor | 33.33% | 7 | 1 | 7 | 1 | 0.00% |
| Trainee SHE reps | 33.33% | 7 | 1 | 7 | 1 | 0.00% |
| Erector | 33.34% | 14 | 14 | 14 | 14 | 0.00% |
|  | 100.00% | 28 | 16 | 28 | 16 | 0.00% |

Number of jobs to be created as a result of this contract is 16

Number of jobs to be Retained as a result of this contract is 0

C1.2 Contract Data

# Part two - Data provided by the Contractor

Notes to a tendering contractor:

- Please read both the NEC3 Engineering and Construction Contract (June 2005) and the relevant parts of its Guidance Notes (ECC3-GN) in order to understand the implications of this Data which the tenderer is required to complete.  An example of the completed Data is provided on pages 152 to 154 of the ECC3 Guidance Notes.

- The number of the clause which requires the data is shown in the left hand column for each statement however other clauses may also use the same data

- Where a form field like this [     ] appears, data is required to be inserted relevant to the option selected. Click on the form field once and type in the data.  Otherwise complete by hand and in ink.

Completion of the data in full, according to Options chosen, is essential to create a complete contract.

| ## Clause | ## Statement | ## Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 10.1 | The Contractor is (Name): |  |  |  |  |  |  |
|  | Address |  |  |  |  |  |  |
|  | Fax No. |  |  |  |  |  |  |
| 11.2(8) | The direct fee percentage is |  |  |  |  |  |  |
|  | The subcontracted fee percentage is |  |  |  |  |  |  |
| 11.2(18) | The working areas are the Site and |  |  |  |  |  |  |
| 24.1 | The Contractor's key persons are: |  |  |  |  |  |  |
|  | 1 Name: |  |  |  |  |  |  |
|  | Job: |  |  |  |  |  |  |
|  | Responsibilities: |  |  |  |  |  |  |
|  | Qualifications: |  |  |  |  |  |  |
|  | Experience: |  |  |  |  |  |  |
|  | 2 Name: |  |  |  |  |  |  |
|  | Job |  |  |  |  |  |  |
|  | Responsibilities: |  |  |  |  |  |  |
|  | Qualifications: |  |  |  |  |  |  |
|  | Experience: |  |  |  |  |  |  |
|  |  | CV's (and further key persons data including CVs) are appended to Tender Schedule entitled . |  |  |  |  |  |
| 11.2(3) | The completion date for the whole of the works is | 30 July 2022 |  |  |  |  |  |
| 11.2(14) | The following matters will be included in the Risk Register | to be defined during Contract execution |  |  |  |  |  |
| 11.2(19) | The Works Information for the Contractor’s design is in: | Part C3: Works Information |  |  |  |  |  |
| 31.1 | The programme identified in the Contract Data is |  |  |  |  |  |  |
| A | Priced contract with activity schedule |  |  |  |  |  |  |
| 11.2(20) | The activity schedule is in | Part C2: Pricing Data |  |  |  |  |  |
| 11.2(30) | The tendered total of the Prices is | (in figures) (in words), excluding VAT |  |  |  |  |  |
| B | Priced contract with bill of quantities |  |  |  |  |  |  |
| 11.2(21) | The bill of quantities is in |  |  |  |  |  |  |
| 11.2(31) | The tendered total of the Prices is | (in figures) (in words), excluding VAT |  |  |  |  |  |
| C | Target contract with activity schedule |  |  |  |  |  |  |
| 11.2(20) | The activity schedule is in | Part C2: Pricing Data |  |  |  |  |  |
| 11.2(30) | The tendered total of the Prices is | (in figures) (in words), excluding VAT |  |  |  |  |  |
| D | Target contract with bill of quantities |  |  |  |  |  |  |
| 11.2(21) | The bill of quantities is in |  |  |  |  |  |  |
| 11.2(31) | The tendered total of the Prices is | (in figures) (in words), excluding VAT |  |  |  |  |  |
| F | Management contract |  |  |  |  |  |  |
| 20.2 | Work which the Contractor’s will do himself is | Activity |  | price (lump sum or rate) |  |  |  |
|  | ## Data for Schedules of Cost Components | Note “SCC” means Schedule of Cost Components starting on page 56 of ECC3, and “SSCC” means Shorter Schedule of Cost Components starting on page 59 of ECC3. |  |  |  |  |  |
| A | Priced contract with activity schedule | Data for the Shorter Schedule of Cost Components |  |  |  |  |  |
| B | Priced contract with bill of quantities | Data for the Shorter Schedule of Cost Components |  |  |  |  |  |
| 41 in SSCC | The percentage for people overheads is: |  |  |  |  |  |  |
| 21 in SSCC | The published list of Equipment is the last edition of the list published by |  |  |  |  |  |  |
|  | The percentage for adjustment for Equipment in the published list is | Minus % |  |  |  |  |  |
| 22 in SSCC | The rates of other Equipment are: In Part C2: Pricing Data | Equipment | Size or capacity |  |  |  | Rate |
| 61 in SSCC | The hourly rates for Defined Cost of design outside the Working Areas are | Category of employee |  |  | Hourly rate |  |  |
|  | Note: Hourly rates are estimated ‘cost to company of the employee’ and not selling rates. |  |  |  |  |  |  |
|  | Please insert another schedule if foreign resources may also be used |  |  |  |  |  |  |
| 62 in SSCC | The percentage for design overheads is |  |  |  |  |  |  |
| 63 in SSCC | The categories of design employees whose travelling expenses to and from the Working Areas are included in Defined Cost are: |  |  |  |  |  |  |
|  | If Option C, D or E is used | Data for Schedule of Cost Components |  |  |  |  |  |
| 23 in SCC | The listed items of Equipment purchased for work on this contract, with an on cost charge, are: | Equipment | Time related charge |  |  | Per (time period) |  |
| 24 in SCC | The rates of special Equipment are: | Equipment | Size or capacity |  |  | Rate |  |
| 44 in SCC | The percentage for Working Areas overheads is: | : |  |  |  |  |  |
| 51 in SCC | The hourly rates for Defined Cost of manufacture or fabrication outside the Working Areas are | Category of employee |  |  | Hourly rate |  |  |
|  | Note: Hourly rates are estimated ‘cost to company of the employee’ and not selling rates |  |  |  |  |  |  |
|  | Please insert another schedule if foreign resources may also be used |  |  |  |  |  |  |
| 52 in SCC | The percentage for manufacture and fabrication overheads is |  |  |  |  |  |  |
|  | If Option C, D, or E is used | Data for both schedules of cost components |  |  |  |  |  |
| 61 in SCC & SSCC | The hourly rates for Defined Cost of design outside the Working Areas are | Category of employee |  |  | Hourly rate |  |  |
|  | Note: Hourly rates are estimated ‘cost to company of the employee’ and not selling rates. |  |  |  |  |  |  |
|  | Please insert another schedule if foreign resources may also be used |  |  |  |  |  |  |
| 62 in SCC & SSCC | The percentage for design overheads is |  |  |  |  |  |  |
| 63 in SCC & SSCC | The categories of design employees whose travelling expenses to and from the Working Areas are included as a cost of design of the works and Equipment done outside the Working Areas are: |  |  |  |  |  |  |
|  | If Option C, D or E is used | Data for the Shorter Schedule of Cost Components |  |  |  |  |  |
| 41 in SSCC | The percentage for people overheads is: |  |  |  |  |  |  |
| 21 in SSCC | The published list of Equipment is the last edition of the list published by |  |  |  |  |  |  |
|  | The percentage for adjustment for Equipment in the published list is |  |  |  |  |  |  |
| 22 in SSCC | The rates of other Equipment are: | Equipment | Size or capacity |  |  |  | Rate |

C1.3 Forms of Securities

- Pro formas for Bonds & Guarantees

- For use with the NEC3 Engineering & Construction Contract (June 2005)

[Note to contract compiler:

Once it has been decided which securities are required for this contract delete from this file the ones not required, revise the notes below accordingly and delete this note.]

The conditions of contract stated in the Contract Data Part 1 include the following Secondary Options:

Option X4:	Parent company guarantee

Option X13:	Performance Bond

Option X14:	Advanced payment to the Contractor

Each of these secondary Options requires a bond or guarantee “in the form set out in the Works Information”.    Pro forma documents for these bonds and guarantees are provided here for convenience but are to be treated as part of the Works Information.

Option X16:	Retention (not used with Option F)

The Contractor may provide a Retention Money Guarantee in the form stated here.  When the Employer receives and accepts a Retention Money Guarantee exactly in the form stated he will instruct the Project Manager not to assess any amount be retained in terms of secondary Option X16.

The Contractor shall guarantee his ASGI-SA Obligations by providing the Employer with an ASGI-SA Guarantee in the form provided here.

[Note to contract compiler:  If there are no ASGI-SA Obligations in this contract, delete the above statement]

The organisation providing the bond / guarantee does so by copying the pro forma document onto his letterhead without any change to the text or format and completing the required details.  The completed document is then given to the Employer within the time stated in the contract.

# Pro forma Parent Company Guarantee (for use with Option X4)

(to be reproduced exactly as shown below on the letterhead of the Contractor’s Parent Company)

| Eskom Holdings SOC Limited Megawatt Park Maxwell Drive Sandton Johannesburg | Date: |  |
| --- | --- | --- |

Dear Sirs,

## Parent Company Guarantee for Contract No

With reference to the above numbered contract made or to be made between

| Eskom Holdings SOC Limited | (the Employer) and |
| --- | --- |
| {Insert registered name and address of the Contractor} | (the Contractor), for |
| {Insert details of the works from the Contract Data} | (the works). |

| I/We the undersigned |  |
| --- | --- |
| on behalf of the Contractor’s parent company |  |
| of physical address |  |

and duly authorised thereto do hereby unconditionally guarantee to the Employer that the Contractor shall Provide the Works in accordance with the above numbered Contract.

- If for any reason the Contractor fails to Provide the Works, we hereby agree to cause to Provide the Works at no additional cost to the Employer.

- If we fail to comply with the terms of this Deed of Guarantee, the Employer may itself procure such performance (whether or not the Agreement be formally determined).  The Employer is to notify us and we shall indemnify the Employer for any additional cost or expense it incurs.

- Our liability shall be as primary obligor and not merely as surety and shall not be impaired or discharged by reason of any arrangement or change in relationship made between the Contractor and the Employer and/or between us and Contractor; nor any alteration in the obligations undertaken by the Contractor or in the terms of the Agreement; nor any indulgence, failure, delay by you as to any matter; nor any dissolution or liquidation or such other analogous event of the Contractor.

- The Employer shall not be obliged before taking steps to enforce the terms of this Deed of Guarantee to obtain judgement against the Contractor in any court or other tribunal, to make or file any claim in liquidation (or analogous proceedings) or to seek any remedy or proceed first against the Contractor.

- This Deed of Guarantee shall be governed by and construed in accordance with the laws of the Republic of South Africa and we hereby submit to the non-exclusive jurisdiction of the Supreme Court of South Africa.

| Signed at |  | on this |  | day of |  | 202_ |
| --- | --- | --- | --- | --- | --- | --- |

| Signature(s) |  |  |
| --- | --- | --- |
| Name(s) (printed) |  |  |
| Position in parent company |  |  |
| Signature of Witness(s) |  |  |
| Name(s) (printed) |  |  |

# Pro forma Performance Bond – Demand Guarantee (for use with Option X13)

(to be reproduced exactly as shown below on the letterhead of the Contractor’s Parent Company)

| Eskom Holdings SOC Limited Megawatt Park Maxwell Drive Sandton Johannesburg | Date: |  |
| --- | --- | --- |

Dear Sirs

Reference No. [●] [Drafting Note: Bank reference number to be inserted]

Performance Bond – Demand Guarantee: [Drafting Note: Name of Contractor to be inserted]

Project [  ] Contract Reference: …… [Drafting Note: Contractor contract reference number to be inserted]

- In this Guarantee the following words and expressions shall have the following meanings:-

  - “Bank” - means [●], [●] Branch, (Registration No. [●]); [Drafting Note: Name of Bank to be inserted]

  - “Bank’s Address” - means [●]; [Drafting Note: Bank’s physical address to be inserted]

  - “Contract” – means the written agreement relating to the Project, entered into between Eskom and the Contractor, on or about the [●] day of [●] 200[●] (Contract Reference No. [.]as amended, varied, restated, novated or substituted from time to time; [Drafting Note: Signature Date and Contract reference number to be inserted]

  - “Contractor” – means [●] a company registered in accordance with the laws of [●] under Registration Number [●]. [Drafting Note: Name and details of Contractor to be inserted]

  - “Eskom” - means Eskom Holdings SOC Limited, a company registered in accordance with the laws of the Republic of South Africa under Registration Number 2002/015527/06].

  - “Expiry Date” - means the date on which the Defects Certificate is issued in terms of the Contract.

  - “Guaranteed Sum” - means the sum of R [●] ([●] Rand);

  - “Project” - means [insert if applicable.].

- At the instance of the Contractor, we the undersigned ______________ and ______________, in our respective capacities as _____________ and ___________ of the Bank, and duly authorized thereto, confirm that we hold the Guaranteed Sum at the disposal of Eskom, as security for the proper performance by the Contractor of all of its obligations in terms of and arising from the Contract and hereby undertake to pay to Eskom, on written demand from Eskom received prior to the Expiry Date, any sum or sums not exceeding in total the Guaranteed Sum.

- A demand for payment under this guarantee shall be made in writing at the Bank’s address and shall:

  - be signed on behalf of Eskom by a director of Eskom or an authorised delegate;

  - state the amount claimed (“the Demand Amount’);

  - state that the Demand Amount is payable to Eskom in the circumstances contemplated in the Contract.

- Notwithstanding the reference herein to the Contract the liability of the Bank in terms hereof is as principal and not as surety and the Bank’s obligation/s to make payment:

  - is and shall be absolute provided demand is made in terms of this bond in all circumstances; and

  - is not, and shall not be construed to be, accessory or collateral on any basis whatsoever.

- The Bank’s obligations in terms of this Guarantee:

  - shall be restricted to the payment of money only and shall be limited to the maximum of the Guaranteed Sum; and

  - shall not be discharged and compliance with any demand for payment received by the Bank in terms hereof shall not be delayed, by the fact that a dispute may exist between Eskom and the Contractor.

- Eskom shall be entitled to arrange its affairs with the Contractor in any manner which it sees fit, without advising us and without affecting our liability under this Guarantee. This includes, without limitation, any extensions, indulgences, release or compromise granted to the Contractor or any variation under or to the Contract.

- Should Eskom cede its rights against the Contractor to a third party where such cession is permitted under the Contract, then Eskom shall be entitled to cede to such third party the rights of Eskom under this Guarantee on written notification to the Bank of such cession.

- This Guarantee:

  - shall expire on the Expiry Date until which time it is irrevocable;

  - is, save as provided for in 7 above, personal to Eskom and is neither negotiable nor transferable;

  - shall be returned to the Bank upon the earlier of payment of the full Guaranteed Sum or expiry hereof;

  - shall be regarded as a liquid document for the purpose of obtaining a court order; and

  - shall be governed by and construed in accordance with the law of the Republic of South Africa and shall be subject to the jurisdiction of the Courts of the Republic of South Africa.

  - Any claim which arises or demand for payment received after expiry date will be invalid and unenforceable.

- The Bank chooses domicilium citandi et executandi for all purposes in connection with this Guarantee at the Bank’s Address.

Signed at _____________________		Date ____________________________

For and behalf of the Bank

Bank Signatory: ___________________		Bank Signatory: ___________________

Witness: ________________________		Witness: _________________________

Bank’s seal or stamp

# Pro forma Advanced Payment Bond (for use with Option X14)

(to be reproduced exactly as shown below on the letterhead of the Bank providing the Bond)

| Eskom Holdings SOC Limited Megawatt Park Maxwell Drive Sandton Johannesburg | Date: |  |
| --- | --- | --- |

Dear Sirs,

## Advanced Payment Bond for Contract No.

With reference to the above numbered contract made or to be made between

| Eskom Holdings SOC Limited | (the Employer) and |
| --- | --- |
| {Insert registered name and address of the Contractor} | (the Contractor), for |
| {Insert details of the works from the Contract Data} | (the works). |

| I/We the undersigned |  |
| --- | --- |
| on behalf of the Surety |  |
| of physical address |  |

and duly authorised thereto do hereby bind ourselves as Surety and co-principal debtors in solidum for the due and proper repayment by the Contractor to the Employer of the advanced payment made by the Employer to the Contractor under the Contract, and for all losses and expenses that may be suffered or incurred by the Employer as a result of non-payment by the Contractor, subject to the following conditions

- The terms Employer, Contractor, and the works have the meaning as assigned to them by the conditions of contract listed in the Contract Data for the aforesaid Contract.

- We renounce all benefits from the legal exceptions "Benefit of Excussion and Division", "No value received" “Revision of Accounts”, “Cession of Action” and any other exceptions which might or could be pleaded against the validity of this bond, with the meaning and effect of which exceptions we declare ourselves to be fully acquainted.

- The Employer has the absolute right to arrange his affairs with the Contractor in any manner which the Employer deems fit and without being advised thereof the Surety shall not have the right to claim his release on account of any conduct alleged to be prejudicial to the Surety.  Without derogating from the foregoing compromise, extension of the construction period, indulgence, release or variation of the Contractor's obligation shall not affect the validity of this Advance Payment bond.

- This bond expires on the date when the Surety receives a notice from the Project Manager stating that the advanced payment has been repaid to the Employer in terms of the Contract, or liquidated by deductions from other payments due to the Contractor.

- The amount of the bond shall be payable to the Employer upon the Employer's demand and no later than 7 days following the submission to the Surety of a certificate signed by the Project Manager stating the amount of the Employer's losses, damages and expenses incurred as a result of the non-performance aforesaid.  The signed certificate shall be deemed to be conclusive proof of the extent of the Employer's loss, damage and expense.

- Our total liability hereunder shall not exceed the sum of ............................. (R ................) which is equal to the advance payment.

- This Advanced Payment Bond is neither negotiable nor transferable and is governed by the laws of the Republic of South Africa.

| Signed at |  | on this |  | day of |  | 200_ |
| --- | --- | --- | --- | --- | --- | --- |

| Signature(s) |  |  |
| --- | --- | --- |
| Name(s) (printed) |  |  |
| Position in Surety company |  |  |
| Signature of Witness(s) |  |  |
| Name(s) (printed) |  |  |

# Pro forma Retention Money Guarantee (may be used when Option X16 applies)

(to be reproduced exactly as shown below on the letterhead of the Bank providing the Guarantee)

| Eskom Holdings SOC Limited Megawatt Park Maxwell Drive Sandton Johannesburg | Date: |  |
| --- | --- | --- |

Dear Sirs

Reference No. [●] [Drafting Note: Bank reference number to be inserted]

Retention Money Guarantee: [Drafting Note: Name of Contractor to be inserted]

Project [  ] : Contract Reference:  [Drafting Note: Contractor contract reference number to be inserted]

- In this Guarantee the following words and expressions shall have the following meanings:-

  - “Bank” - means [●], [●] Branch, (Registration No. [●]); [Drafting Note: Name of Bank to be inserted]

  - “Bank’s Address” - means [●]; [Drafting Note: Bank’s physical address to be inserted]

  - “Contract” – means the written agreement relating to the Project, entered into between Eskom and the Contractor, on or about the [●] day of [●] 200[●] (Contract Reference No. ………. as amended, varied, restated, novated or substituted from time to time; [Drafting Note: Signature Date and Contract reference number to be inserted]

  - “Contractor” – means [●] a company registered in accordance with the laws of [●] under Registration Number [●]. [Drafting Note: Name and details of Contractor to be inserted]

  - “Eskom” - means Eskom Holdings SOC Limited, a company registered in accordance with the laws of the Republic of South Africa under Registration Number 2002/015527/06

  - “Expiry Date” - means the date on which the Defects Certificate is issued in terms of the Contract.

  - “Guaranteed Sum” - means the sum of R [●] ([●] Rand); [Drafting Note: Insert amount of Retention Money Guarantee.].

  - “Project” - means the…………………………………..

- At the instance of the Contractor, we the undersigned ______________ and ______________, in our respective capacities as _____________ and ___________ of the Bank, and duly authorized thereto, confirm that we hold the Guaranteed Sum at the disposal of Eskom, as security for the proper performance by the Contractor of all of its obligations in terms of and arising from the Contract and hereby undertake to pay to Eskom, on written demand from Eskom received prior to the Expiry Date, any sum or sums not exceeding in total the Guaranteed Sum.

- A demand for payment under this guarantee shall be made in writing at the Bank’s address and shall:

  - be signed on behalf of Eskom by a director of Eskom or his authorised delegate.

  - state the amount claimed (“the Demand Amount’);

  - state that the Contractor has failed to carry out his obligation(s) to rectify certain defect(s) for which he is responsible under the Contract (and the nature of such defect(s)) alternatively that the Demand Amount is payable to Eskom in the circumstances contemplated in the Contract.

- Notwithstanding the reference herein to the Contract the liability of the Bank in terms hereof is as principal and not as surety and the Bank’s obligation/s to make payment:

  - is and shall be absolute provided demand is made in terms of this bond in all circumstances; and

  - is not, and shall not be construed to be, accessory or collateral on any basis whatsoever.

- The Bank’s obligations in terms of this Guarantee:

  - shall be restricted to the payment of money only and shall be limited to the maximum of the Guaranteed Sum; and

  - shall not be discharged and compliance with any demand for payment received by the Bank in terms hereof shall not be delayed, by the fact that a dispute may exist between Eskom and the Contractor.

- Eskom shall be entitled to arrange its affairs with the Contractor in any manner which it sees fit, without advising us and without affecting our liability under this Guarantee. This includes, without limitation, any extensions, indulgences, release or compromise granted to the Contractor or any variation under or to the Contract.

- Should Eskom cede its rights against the Contractor to a third party where such cession is permitted under the Contract, then Eskom shall be entitled to cede to such third party the rights of Eskom under this Guarantee on written notification to the Bank of such cession.

- This Guarantee:

  - shall expire on the Expiry Date until which time it is irrevocable;

  - is, save as provided for in 7 above, personal to Eskom and is neither negotiable nor transferable;

  - shall be returned to the Bank upon the earlier of payment of the full Guaranteed Sum or expiry hereof;

  - shall be regarded as a liquid document for the purpose of obtaining a court order; and

  - shall be governed by and construed in accordance with the law of the Republic of South Africa and shall be subject to the jurisdiction of the Courts of the Republic of South Africa.

  - Any claim which arises or demand for payment received after expiry date will be invalid and unenforceable.

- The Bank chooses domicilium citandi et executandi for all purposes in connection with this Guarantee at the Bank’s Address.

Signed at _____________________		Date ____________  Bank’s seal or stamp

For and behalf of the Bank

Bank Signatory: ___________________		Bank Signatory: ___________________

Witness: ________________________		Witness: _________________________

# Pro forma ASGI-SA Guarantee

(to be reproduced exactly as shown below on the letterhead of the Bank providing the Guarantee)

| Eskom Holdings SOC Limited Megawatt Park Maxwell Drive Sandton Johannesburg | Date: |  |
| --- | --- | --- |

Dear Sirs

Reference No. [●] [Drafting Note: Bank reference number to be inserted]

Pro-Forma ASGI-SA  Guarantee: [Drafting Note: Name of Contractor to be inserted]

Project [  ] Contract Reference: [●] [Drafting Note: Contractor contract reference number to be inserted]

- In this Guarantee the following words and expressions shall have the following meanings:-

  - “Bank” - means [●], [●] Branch, (Registration No. [●]); [Drafting Note: Name of Bank to be inserted]

  - “Bank’s Address” - means [●]; [Drafting Note: Bank’s physical address to be inserted]

  - “Contract” – means the written agreement relating to the Project, entered into between the Employer and the Contractor, on or about the [●] day of [●] 200[●] (Contract Reference No. [●] as amended, varied, restated, novated or substituted from time to time; [Drafting Note: Signature Date and Contract reference number to be inserted]

  - “Contractor” – means [●] a company registered in accordance with the laws of [●] under Registration Number [●]. [Drafting Note: Name and details of Contractor to be inserted]

  - “Contractor’s ASGI-SA Obligations” – means the Contractor’s ASGI-SA Obligations under and as defined in the Contract.

  - “Employer” - means Eskom Holdings SOC Limited, a company registered in accordance with the laws of the Republic of South Africa under Registration Number 2002/015527/06.

  - “Expiry Date” - means the [●] day of [●] 200[●]; [Drafting Note: anticipated date of issue of ASGI-SA Performance Certificate to be inserted.]

  - “Guaranteed Sum” - means the sum of R [●] ([●] Rand);

  - “Project” – means the …………………………

- At the instance of the Contractor, we the undersigned ______________ and ______________, in our respective capacities as _____________ and ___________ of the Bank, and duly authorized thereto, confirm that we hold the Guaranteed Sum at the disposal of the Employer, as security for the proper performance by the Contractor of the Contractor’s ASGI-SA Obligations and hereby undertake to pay to the Employer, on written demand from the Employer received prior to the Expiry Date, any sum or sums not exceeding in total the Guaranteed Sum.

- A demand for payment under this guarantee shall be made in writing at the Bank’s address and shall:

  - state the amount claimed (“the Demand Amount’);

  - state that the Demand Amount is payable to the Employer in the circumstances contemplated in the Contract.

- Notwithstanding the reference herein to the Contract the liability of the Bank in terms hereof is as principal and not as surety and the Bank’s obligation/s to make payment:

  - is and shall be absolute provided demand is made in terms of this bond in all circumstances; and

  - is not, and shall not be construed to be, accessory or collateral on any basis whatsoever.

- The Bank’s obligations in terms of this Guarantee:

  - shall be restricted to the payment of money only and shall be limited to the maximum of the Guaranteed Sum; and

  - shall not be discharged and compliance with any demand for payment received by the Bank in terms hereof shall not be delayed, by the fact that a dispute may exist between the Employer and the Contractor.

- The Employer shall be entitled to arrange its affairs with the Contractor in any manner which it sees fit, without advising us and without affecting our liability under this Guarantee. This includes, without limitation, any extensions, indulgences, release or compromise granted to the Contractor or any variation under or to the Contract.

- Should the Employer cede its rights against the Contractor to a third party where such cession is permitted under the Contract, then the Employer shall be entitled to cede to such third party the rights of the Employer under this Guarantee on written notification to the Bank of such cession.

- This Guarantee:

  - shall expire on the Expiry Date until which time it is irrevocable;

  - is, save as provided for in 7 above, personal to the Employer and is neither negotiable nor transferable;

  - shall be returned to the Bank upon the earlier of payment of the full Guaranteed Sum or expiry hereof;

  - shall be regarded as a liquid document for the purpose of obtaining a court order; and

  - shall be governed by and construed in accordance with the law of the Republic of South Africa and shall be subject to the jurisdiction of the courts of the Republic of South Africa.

  - Any claim which arises or demand for payment received after expiry date will be invalid and unenforceable.

- The Bank chooses domicilium citandi et executandi for all purposes in connection with this Guarantee at the Bank’s Address.

Signed at _____________________		Date ____________________________

For and behalf of the Bank

Bank Signatory: ___________________		Bank Signatory: ___________________

Witness: ________________________		Witness: _________________________

Bank’s seal or stamp

Part 2: Pricing Data

| Document reference | Title | No of pages |
| --- | --- | --- |
| C2.1 | Pricing assumptions: Option A |  |
| C2.2 | The activity schedule |  |

C2.1 Pricing assumptions: Option A

# The conditions of contract

## How work is priced and assessed for payment

Clause 11 in NEC3 Engineering and Construction Contract, June 2005 (ECC3) Option A states:

| Identified and defined terms | 11 11.2 | (20) The Activity Schedule is the activity schedule unless later changed in accordance with this contract. |
| --- | --- | --- |
|  |  | (27) The Price for Work Done to Date is the total of the Prices for - each group of completed activities and - each completed activity which is not in a group. A completed activity is one which is without Defects which would either delay or be covered by immediately following work. |
|  |  | (30) The Prices are the lump sum prices for each of the activities on the Activity Schedule unless later changed in accordance with this contract. |

This confirms that Option A is a lump sum form of contract where the work is broken down into activities, each of which is priced by the tendering contractor as a lump sum.   Only completed activities are assessed for payment at each assessment date; no part payment is made if the activity is not completed by the assessment date.

## Function of the Activity Schedule

Clause 54.1 in Option A states: “Information in the Activity Schedule is not Works Information or Site Information”.  This confirms that instructions to do work or how it is to be done are not included in the Activity Schedule but in the Works Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Works in accordance with the Works Information”. Hence the Contractor does not Provide the Works in accordance with the Activity Schedule.  The Activity Schedule is only a pricing document.

## Link to the programme

Clause 31.4 states that “The Contractor provides information which shows how each activity on the Activity Schedule relates to the operations on each programme which he submits for acceptance”.  Hence when compiling the activity schedule, the tendering contractor needs to show each activity on the programme he submits with his tender.

## Preparing the activity schedule

The tendering contractor prepares the activity schedule and should study the ECC3 Guidance Notes pages 19 and 20 before doing so.  The Employer may have instructed the tendering contractor to include particular activities which he has specified and requires the Contractor to identify them in his activity schedule.

      - Generally it is the Contractor who prepares the Activity Schedule as part of his tender by breaking down the work described within the Works Information into suitable activities which can be well defined, priced as a lump sum and shown on the programme.  The Employer, in his Conditions of Tender or in a Tender Schedule, may have listed some items that he requires the Contractor to include in his activity schedule and be priced accordingly.

      - The Prices are defined in clause 11.2(20) as the lump sum for each activity in the activity schedule and the Price for Work Done to Date (PWDD) (the amount due to the contractor) is defined in clause 11.2(24) as the total of the Prices for each activity that has been completed.  Hence activities in the activity schedule should be structured so as to provide an acceptable monthly cash flow as they are only assessed for payment on the assessment date if they have been completed.

      - As the Contractor has an obligation to correct Defects (core clause 43.1) and there is no compensation event for this unless the Defect was due to an Employer’s risk, the lump sum Prices must also include for the correction of Defects.

      - If the Contractor has decided not to identify a particular activity, the cost to the Contractor of doing the work must be included in, or spread across, the other Prices in order to fulfil the obligation to complete the works for the tendered total of the Prices.

      - There is no adjustment to the lump sum activity schedule price if the amount, or quantity, of work within that activity later turns out to be different to that which the contractor estimated at time of tender. The only basis for a change to the Prices is as a result of a compensation event. See Clause 60.1.

      - Hence the Prices tendered by the Contractor in the activity schedule are inclusive of everything necessary and incidental to Providing the Works in accordance with the Works Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk.

      - However, the Contractor does not have to allow in his Prices for matters that may arise as a result of a compensation event.  It should be noted that the list of compensation events includes those arising as a result of an Employer's risk event listed in core clause 80.1.

C2.2 the activity schedule

Use this page as a cover page to the Contractor’s activity schedule.

Part 3: Scope of Work

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C3.1 | Employer’s Works Information |  |
| C3.2 | Contractor’s Works Information (insert at award stage or delete if not applicable) |  |
|  | Total number of pages | 32 |

C3.1: Employer’s works Information

Contents

Part 3: Scope of Work	2

C3.1: Employer’s works Information	3

1	Description of the works	5

1.1	Employer’s objectives and purpose of the works	5

1.2	Interpretation and terminology	5

2	Management and start up.	6

2.1	Management meetings	6

2.2	Documentation control	6

2.3	Health and safety risk management	6

2.4	Environmental constraints and management	7

2.5	Quality assurance requirements	8

2.6	Programming constraints	8

2.7	Invoicing and payment	8

2.8	Contract change management	9

2.9	Provision of bonds and guarantees	9

3	Engineering and the Contractor’s design	10

3.1	Employer’s design	10

3.1.1	High security fence and gates	10

3.2	Parts of the works which the Contractor is to design	10

3.2.1	Kiosk Fire detector	10

3.3	Procedure for submission and acceptance of Contractor’s design	17

3.4	As-built drawings, operating manuals and maintenance schedules	17

4	Procurement	19

4.1	People	19

4.1.1	Minimum requirements of people employed on the Site	19

4.1.2	BBBEE and preferencing scheme	19

4.1.3	Accelerated Shared Growth Initiative – South Africa (ASGI-SA)	19

4.2	Subcontracting	19

4.3	Plant and Materials	19

4.4	Tests and inspections before delivery	19

5	Construction	20

5.1	Temporary works, Site services & construction constraints	20

5.1.1	Employer’s Site entry and security control, permits, and Site regulations	20

5.1.2	Restrictions to access on Site, roads, walkways and barricades	20

5.1.3	People restrictions on Site; hours of work, conduct and records	20

5.1.4	Health and safety facilities on Site	20

5.1.5	Environmental controls, fauna & flora, dealing with objects of historical interest	20

5.1.6	Title to materials from demolition and excavation	20

5.1.7	Cooperating with and obtaining acceptance of Others	21

5.1.8	Publicity and progress photographs	21

5.1.9	Contractor’s Equipment	21

5.1.10	Equipment provided by the Employer	21

5.1.11	Site services and facilities	21

5.1.12	Facilities provided by the Contractor	21

5.1.13	Existing premises, inspection of adjoining properties and checking work of Others	21

5.1.14	Survey control and setting out of the works	21

5.1.15	Excavations and associated water control	21

5.1.16	Underground services, other existing services, cable and pipe trenches and covers	22

5.1.17	Control of noise, dust, water and waste	22

5.1.18	Giving notice of work to be covered up	22

5.1.19	Hook ups to existing works	22

5.2	Completion, testing, commissioning and correction of Defects	22

5.2.1	Materials facilities and samples for tests and inspections	22

5.2.2	Commissioning	22

5.2.3	Take over procedures	22

5.2.4	Access given by the Employer for correction of Defects	22

5.2.5	Performance tests after Completion	23

5.2.6	Training and technology transfer	23

6	Plant and Materials standards and workmanship	24

6.1	Building works	24

6.2	Civil engineering and structural works	24

6.3	Electrical & mechanical engineering works	24

6.4	Process control and IT works	24

7	List of drawings	25

7.1	Drawings issued by the Employer	25

C3.2	Contractor’s Works Information	26

# Description of the works

## Employer’s objectives and purpose of the works

The Employer (Eskom Holdings Limited) is the South African power utility.

The Employer’s high level scope is as follows:

- Supply ,Install and commission Control Kiosks and Fire Detection System

- Supply of all design drawings, operational manuals and maintenance manuals

- Training of Employer personnel

This document details the Employer’s requirements in terms of:

I.•	Functionality

II.•	Performance

III.•	Environment

IV.•	Training

V.•	Maintenance and Spares

VI.•	Procurement

## Interpretation and terminology

The following abbreviations are used in this Works Information:

| Abbreviation | Meaning given to the abbreviation |
| --- | --- |
| AFC | Approved for construction |
| OBL | Outside battery limits |

# Management and start up.

## Management meetings

Site Inaugural meeting will be held on site two (2) weeks prior to commencement of site activities and the contractor shall avail safety file for auditing purposes.

Project progress meetings will be held once every fortnight on site in order to track work progress, safety, environmental and other issues. A contractor must avail himself to these meetings.

Meetings of a specialist nature may be convened at times and locations to suit the Parties, the nature and the progress of the works.  Records of these meetings shall be submitted to the Project Manager by the person convening the meeting within five days of the meeting.

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.

## Documentation control

The documentation supplied by the Contractor shall include be in both hard copy and electronic form. A minimum of three hard copies will be provided. Each document shall include, at a minimum, the following information:

•	Title

•	Status

•	Revision

•	References

•	Purpose

•	Description

## Health and safety risk management

The Contractor shall at all times comply with the health and safety requirements prescribed by law as they may apply to the works.  The Contractor shall comply with the health and safety requirements contained in in the following documents:

- SHEQ policy:– 32 -727

- Eskom Procurement and supply chain management procedure – 32-1034

- SHE Requirements for the Eskom Commercial process – 32- 726

- Contractor health and safety requirements – 32-136

- Integrated SHE organisation: roles and responsibilities and statutory appointments – 32-296

- Life saving rules – 240-62196227

- Working at heights – 32-418

- Eskom Vehicle safety specification – 32-345

- Employer’s Health and Safety requirements - TST32-136

The authorization procedure for a permit to work shall be followed by the Contractor before commencing work on site. It is the Contractor’s responsibility to ensure that a permit to work is obtained before access to the work can be given. It is the Contractor’s responsibility to also ensure that the safety file has been audited by the Health and Safety Representatives before establishing site.

The Contractor must be in possession of current first aid certificate. The Contractor’s trucks must have a valid and current crane test certificate with the truck driver and crane operator’s certificate. All tools must have valid and current test certificates, which must be produced two weeks before site establishment.

The Contractor will only leave site once a written site instruction has been issued by an Eskom site representative. Working hours will be from 08h00 to 16h00 during week days, weekend work to be carried out only on request by Eskom.

The Contractor is to have an Eskom certified and authorized person available in each area where work is being performed at all times in accordance with Eskom transmission standard TST32-136 contractor safety in a high voltage environment.

A complete safety and risk assessment must be done BEFORE the contractor starts works on site. The Site Supervisor will be monitoring the works continuously to ensure strict adherence to Safety rules. If needed, the contractor is to visit the site at the Contractor’s own cost before work commences to familiarize with the scope of works and to assess any safety issues.

Before any excavation is commenced, it will be the responsibility of the Contractor to ascertain from the Site Supervisor the position of any existing services on site.  Once these are indicated to the contractor they shall be deemed “known”.  Any costs incurred for repairs to any “known” services shall be for the contractor’s account.

The Contractor shall allow safe access for other contractors and Eskom personnel when required.

The Contractor shall establish a refuse control system.  All waste is to be collected and disposed of as required by Eskom and the local authority.

The Contractor shall make his own arrangements for the provision of accommodation for his employees.

## Environmental constraints and management

The Contractor is required to ensure that all goods, services or works supplied in terms of the tender/contract/order conform to all applicable environment legislation, Authorisations, EPC32-727: Eskom SHEQ Policy, ST32-726: SHE Requirements for the Eskom Commercial Process (additional requirements) and Project Specific Environmental Management Plan (EMP).

The Contractor shall control his activities and processes in accordance with Eskom’s Environmental Policies: TST41-120 (rev 2). The Eskom EMP provides the Aspects and Impacts that will require management and must be followed strictly.  The Contractor shall prepare a separate mitigation plan for all environmental concerns raised through the EMP and in any other relevant forum. The contractor must develop method statements based on the EMP. All developed method statements must be approved by the Employer.

Any changes to the approved EMP shall be reported and approved by (BUER) and Project Manager prior to the commencement of work and during construction.. The supplier must ensure that all sub-contractors’ environmental management programmes comply with the contract shall define the specific system elements applicable to the subcontractor’s scope of work or supply.

Environmental meetings between Eskom and the Contractor may be held regularly and copies of the minutes may be submitted to Eskom on request. The contractor is to send a flash report for any environmental incidences that has occurred on site as soon as possible or within 24 hours to the SS /Grid Environmental and PM clearly stating any impact to the environment.

Contractor must now sign-off TRM-FM-0038 – Eskom Holdings Transmission division contractor environmental compliance Proformas.

If waste is generated during project, it must be disposed at a registered site and contractor shall retain records of disposal.

The contractor shall conform to requirements from the following documents:

•	Eskom SHEQ Policy (EPC 32-727)

•	Eskom Environmental Management plan

•	TST41-120 rev 2 (Environmental Requirements for the Procurement of Assets, Goods and Services

•	Please attach ST32-726 for additional SHE requirements

•	TRM-FM 0081 – Environmental Tender evaluation form

•	TRM-FM 0038 – Contractor Environmental Compliance

The Contractor shall comply with the environmental criteria and constraints stated in the Eskom Environmental Management plan. Returnable shall include:

•	End of life cycle of equipment (disposal method).

•	Specification for the equipment and inform Eskom of any hazardous components/substances

•	Refer to   TRM-FM 0081 – Environmental Tender evaluation form for other tender returnable

## Quality assurance requirements

The following standards contain provisions that, through reference in this text, constitute provisions of this specification. At the time of publication the revisions indicated were valid.

All standards are subject to review, and parties entering into service agreements based on this specification are encouraged to investigate the possibility of applying the most recent revisions of the standards listed below. Information on currently valid national and international standards may be obtained from the Information Centre at Megawatt Park and Technology Standardisation Department.

In the event of conflict between documents invoked here and the contents of this specification, the contents of this specification shall be considered to have preference. Such conflict shall be pointed out to the Employer for confirmation.

- Project Quality plan

The Employer requires that the Contractor operate a quality management system as stated in the Scope.

The Employer requires that the Contractor provide a quality policy statement and quality plan which complies with requirements stated in the Scope.

## Programming constraints

The Contractor shall include all stages including deliverables per stage in the programme. The programme shall be submitted to the Employer for acceptance in MS Projects format.

## Invoicing and payment

The following details shall be shown on or attached to each Invoice to show how the amount due has been assessed:

The Contractor shall address the tax invoice to ESKOM HOLDINGS SOC LIMITED (Reg No. 2002/015527/30) and include on each invoice the following information

•	Name and address of the Contractor and the Employer’s Agent;

•	Contractor’s VAT registration number;

•	The Employer’s VAT registration number 4740101508;

•	Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

•	Other amounts to be paid to the Contractor;

•	Less amounts to be paid by or retained from the Contractor;

•	The change in the amount due since the previous payment being the invoiced amount - excluding VAT, the VAT and including VAT;

The Contractor attaches the detailed assessment of the amount due to each tax invoice showing the Price for Work Done to Date for each item in the Price List for work which he has completed.

A tax invoice shall be submitted on completion of the works in the format required.  A breakdown of all work completed during the previous period shall be attached.  Invoicing and relevant details will be discussed at site hand-over meeting.  Payments will be processed once all completion certificates and invoices are submitted

## Contract change management

Defined costs are actual costs incurred by the Contractor. These costs should not include profit or company overheads. All compensation events will only be paid on defined costs.

In an event of labour costs, the Contractor is required to provide pay slips of the employees used. The labour mark-up indicated in this contract will be added to these actual costs to form the final value of the compensation event.

In the event that the Contractor is required to supply anything other than people, the Contractor is required to provide a copy of his Contractors invoice. The profit and overhead mark-up indicated in this contract will be added to these actual costs to form the final value of the compensation event.

Copies of payslips and Contractors invoices are to accompany the requests for compensation events.

The Contractor shall under no circumstances refuse additional work on the basis of costs as defined above

## Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Project Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract.

# Engineering and the Contractor’s design

## Employer’s design

### Kiosk fire detector

The Employer is issuing requirements to the Contractor as specified in the PTM&C Design Report, HYD19PO5-P-87. This report discusses a fire detection system that can be installed inside the stand-alone control kiosks at Hydra MTS to identify fire hazard conditions and therefore limit damage to substation protection and automation equipment

## Parts of the works which the Contractor is to design

### Kiosk Fire detector

- The fire detection and alarm system will be designed to facilitate accurate identification of the source of heat / smoke / fire in their early stages to minimize occurrences of false alarms due to faulty equipment, electrical transients, system faults etc.

- The fire alarm control panels will make final decision on whether a fire or fault exists by comparing the plotted patterns from a fire sensor against known fire and fault patterns held in its memory.

- Ensure that the smoke alarm/fire alarm is marshalled to the ERTU and communicated to local and remote control systems and any alarms should be tested as part of the commissioning of the system.

- The smoke/fire alarm should be marshalled together with the over/temperature alarm for system reliability.

A simplified block diagram for the system is shown in the figure below:

#### Installation requirements

- Install a fire detection system in each stand-alone protection kiosk at Hydra MTS.

- Fire detection components will be installed inside the Kiosk and associated drawings will be updated to indicate installations.

- Wire the system to the power distribution board and fire and air conditioner alarm panel.

- Supply and install necessary conduit, enclosed truncking and wiring for the smoke detection and fire alarm system.

- All cables associated with the smoke detection and fire alarm system should be of the fire resistant 1.5sq mm type.

- All wiring will be installed to provide complete and satisfactory function system in all respects.

- All cable terminations at components and junction boxes will have identification tags, indicating throughout the system as per Eskom standards.

- After the installation is complete, the contractor will conduct operating and commissioning tests.

- The equipment will be demonstrated to operate in accordance with the requirements of the specification.

- The system installation, testing and commissioning will be as per Local approvals and requirements.

- The fire alarm system will be completely programmed in accordance with Fire Department requirement.

- A company trained representative will personally supervise the complete installation and final testing of the system.

- All tests will be carried out in the presence of the Client or persons authorized by the consultant/client.

- Upon the completion of the acceptance tests, the representatives will instruct operatives in the proper operation, maintenance programming, configuration, and testing of the system.

- The vendor will provide equipment and/or software which is necessary to allow field modification of the programming and configuration.

#### Product Life Cycle Requirements

- Design

Although standardized design components will be used, design requirements are unique to a specific site. A site survey with all relevant stakeholders must take place to ensure that the supplier familiarize himself with specific site conditions and customer requirements.

The following supplier specific standardized design components and drawings must be accepted by Eskom:

- Sensors that will integrate to the existing control system.

- AC reticulation and control wiring.

- Installation and commissioning procedure.

#### Installation and inspection

- Installation

- Procedures should be covered in the Quality Management System.

- Detailed installation and training documentation should be available.

- Installers must be declared competent and be accredited by the supplier. Relevant detail of installers must be available. This includes, training received, level of expertise and project involvement.

- Hold and inspection points must be clearly specified.

- Inspection

- Final inspection must be done by both the Customer and Supplier. Standardized check sheets shall be documented in the suppliers Quality Management system

- A final certificate of compliance (indicating the warrantee) shall be issued to the customer by the supplier.

#### Maintenance and Repair

- Maintenance

- Maintenance philosophies must be documented by the supplier and indicate nature of inspection, interval treatment, and repair.

#### Quality Management System and Guarantee

- Quality Management System

- The supplier shall have a documented and maintained Quality Management System.

- Eskom will audit the suppliers Quality management system in accordance with the Supplier Contract Quality document QM-58.

- The supplier shall submit the quality control plans to Eskom, indicating all inspection and hold points, sample size, and “pass/fail” criteria. The plans must be accepted by Eskom.

- The scope must encompass all activities that the supplier will be involved with from design to commisioning. The following activities must be covered in detail.

  - Design

  - Supply

  - Install

  - Commission

- Guarantee

- The supplier shall guarantee the fire detection system and the installation thereof.

- The supplier shall state the minimum Guarantee duration.

- The supplier shall in detail document what constitutes a “failure”.

#### Eskom substations diverse and harsh environment

The conditions described below shall be taken as those which all systems and associated equipment should be able to withstand without the performance being out of limits or the life cycle being shortened: -

- Altitude:

- 0 – 2500 meters

- Ambient temperature:

- -40 to + 700C

- Relative Humidity:

- Up to 100% outdoors, 5 to 95% indoors in the specified temperature range.

- Static voltage environment:

- Equipment should be able to withstand volatile static environment and stipulate special earthing practices if required for the safe operation of their equipment.

#### Installation and commissioning

Eskom Transmission documentation will be applicable during installation and commissioning including the use of certain equipment/material such as fibre optic etc. Contractors shall indicate to Eskom if installation method or equipment conflicts with Eskom requirements

Contractors shall provide all equipment associated with installation and commissioning. The contractor will be responsible for providing all access equipment necessary to enable safe installation of all high level equipment and cabling. The installation will comply with all relevant SABS and other applicable international regulations such as follows: -

- The requirements of BS 7671 1992 (16th Edition 1991 Wiring Regulations for Electrical Installations as issued by the Institute of Electrical Engineers) "The Requirements for Electrical Installations".

- Installation will comply with NACOSS NACP20 " Code of practice for planning, installation and maintenance of Closed Circuit Television Systems".

Where mains wiring is applicable in this installation, this must be installed by a certified qualified electrician.

- All equipment is to be pre-built and tested at the contractor's premises before being delivered to site.

- The contractor is responsible for ensuring that a complete working system according Eskom requirements is provided for Transmission substations.

#### In-house manufactured equipment

All equipment to be provided for this tender must be based on open/international standards, generally available products. This is to ensure that the future extensions to the system may be carried out by any installing company extending the controls by adding cards, cages, etc. The use of specialised in-house manufactured components will not be acceptable. This does not preclude the use of 'badged' products, providing the manufacturers are clearly stated and the product has not been modified or customised in any way.

#### Sub-contracting

No part of the contract may be sub-contracted to any other company or individuals without the express written permission of Eskom Transmission. Unless specified to the contrary, it is assumed that all work will be carried out by the contractor’s direct labour. If it is intended to sub-contract any part of the design or installation, this must be made clear in the tender submission and the name of the sub-contractor(s) must be provided. Eskom Transmission reserves the right to accept or reject nominated sub-contractors.

#### Warranty period

The Contractor will repair, correct, or replace any defect of any nature that may occur for a period of twelve months from the date of the issue of the Certificate of Practical Completion. To this end, the Contractor will attend site within 8 hours of the fault being reported. The defect will be corrected without undue delay. To this end, the contractor will hold sufficient stock of spares to allow speedy repair or replacement of equipment. Waiting for manufacturers to replace or repair equipment will not be acceptable.

The Contractor will provide the employer with details of telephone and fax facilities for reporting such defects. The warranty is to include for full maintenance in accordance with the manufacturer’s’ recommendations. The contractor will have in operation a system whereby all service visits are recorded on a multi-part form, a copy of which will be left on site. The form will record the date and time of the fault being reported, the nature of the reported fault, the date and time of the visit and the actual fault together with the remedial work carried out. The supplier must also state their after-warranty support contract, repair of spares turnaround time.

## Procedure for submission and acceptance of Contractor’s design

The contractor must submit the following items:

- Any other relevant drawings,

- Operating manuals

- Maintenance schedules

The plans must be submitted to the project manager for approval and his/her acceptance prior to any work commencing. The drawings must be submitted in electronic pdf format during design phase, correctly annotated and titled with description, date, and reference numbers and A3 or larger size paper. The pdf drawings shall be submitted one week after contract award.

All designs must be presented to the relevant approval committees for acceptance/approval.

## As-built drawings, operating manuals, and maintenance schedules

Information and wording on drawings shall be in English.

The following drawings shall be submitted when a contract is awarded:

- Any other relevant drawings

- Operating manuals

- Maintenance schedules

Service manuals shall be provided before delivery and shall contain all information and procedures necessary for maintenance personnel to carry out routine preventative maintenance.

Service manuals shall be in hardcover, loose-leaf form and/or software copies.  Any modifications thereto shall be described in detail, as a supplement to the service manual.

The Supplier shall provide five copies, in English, of each of the installation and maintenance manuals, and final A3 drawings will be submitted during project handover.

# Procurement

## People

### Minimum requirements of people employed on the Site

Eskom Substations are National Key points therefore all the people working on Eskom sites should be vetted before commencement of the work. Copy of the ID documents should be contained on site safety file. People employed on site shall have all relevant documents as required by law for employment within the country, i.e. relevant work permits and Identifications.

# 4.1.2 Supplier Development and Localisation (SD&L) applicable

Eskom SOC Limited as an organ of State is required to implement South African Government Policy in a number of areas. SD&L is the South African Government’s accelerated shared growth initiative. The initiative has identified Government spending on infrastructure – such as power station construction - as a key area for SD&L intervention and Eskom Holdings Limited is accordingly required to set skills development and local content targets and minimums as key evaluation criteria in tenders that it awards.

Eskom SOC Limited has long had a policy in place regarding procurement from black individuals and companies owned and controlled by black individuals. This policy is number 32-416 “Implementation of Eskom’s Black Economic Empowerment Strategy” which is in line with The Codes of Good Practice gazetted by the Minister of Trade and Industry on the 9 February 2007. For the purposes of this tender the targets for black procurement have been set both as part of the SD&L evaluation and as part of commercial evaluation of whether the Contractor meets the Required BEE score. The SD&L requirements only are discussed in this document.

For this tender all tenderers must demonstrate at least a sixty percent (60%) overall SD&L score for their tender to be evaluated. SD&L compliance is given twenty three percent (23%) of the total tender points and as such, this is a key evaluation criterion for the tender. A scorecard approach to measuring the SD&L compliance of tenderers is followed and a weighting is given to each aspect of SD&L.

For the purposes of tendering, the tenderer must demonstrate the manner in which the SD&L requirements will be met in due course in an implementation program. If the tender is awarded all SD&L undertakings (the Contractor’s SD&L Obligations) must be made by the Contractor at the time of contracting.

### BBBEE and preferencing scheme

Total points for Price and B-BBEE must not exceed 10Failure on the part of a tenderer to fill in and/or to sign this form and submit a B-BBEE Verification Certificate from a Verification Agency accredited by the South African Accreditation System (SANAS) or a Registered Auditor approved by the Independent Regulatory Board of Auditors (IRBA) or an Accounting Officer as contemplated in the Close Corporation Act (CCA) together with the tender, will be interpreted to mean that preference points for B-BBEE status level of contribution are not clear. The purchaser reserves the right to require either of a tenderer, before a tender is adjudicated or at any time subsequently, to substantiate any claim about preferences, in any manner required by the purchaser.

### Accelerated Shared Growth Initiative – South Africa (ASGI-SA)

The Contractor complies with and fulfils the Contractor’s obligations in respect of the Accelerated and Shared Growth Initiative - South Africa in accordance with and as provided for in the Contractor’s ASGI-SA Compliance Schedule stated below.

[Insert the agreed ASGI-SA Compliance Schedule here]

The Contractor shall keep accurate records and provide the Project Manager with reports on the Contractor’s actual delivery against the above stated ASGI-SA criteria.   [Elaborate on access to and format of records and frequency of submission etc.]

The Contractor’s failure to comply with his ASGI-SA obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.

## Subcontracting

### Preferred subcontractors

As per Eskom procurement documents

### Subcontract documentation, and assessment of subcontract tenders

As per Eskom procurement documents

### Limitations on subcontracting

As per Eskom procurement documents

### Attendance on subcontractors

As per Eskom procurement documents

## Plant and Materials

### Quality

Quality requirements are described in the Project Quality Plan document number 240-76368574 and the Supplier Quality Management standard, document number 240-105658000 standard.

### Plant & Materials provided “free issue” by the Employer

Not applicable

### Contractor’s procurement of Plant and Materials

As per Eskom procurement documents

### Spares and consumables

Not applicable to this contract

## Tests and inspections before delivery

Eskom reserves the right to inspect any task performed at any given time. Therefore, Eskom or its appointed representatives shall have access to the works as and when required to carry out any inspection. Inspection at hold –points, as indicated on the inspection and Test Plan to be submitted by the Contractor, are mandatory.

## Marking Plant and Materials outside the Working Areas

The Contractor shall mark all Equipment, Plant and Material that is outside of the working area for the works.

## Contractor’s Equipment (including temporary works).

Not applicable to this contract

## Tests and inspections before delivery

Requirements are described in the Project Quality Plan document number 240-76368574 and the Supplier Quality Management standard, document number 240-105658000 standard.

# Construction

## Temporary works, Site services & construction constraints

### Employer’s Site entry and security control, permits, and Site regulations

As explained/mentioned on Site information document, access to the Eskom Premises should be pre-arranged with the Eskom representative or Supervisor and the contractor employees should always carry the ID documents with them. Once again, the contractor employees should be vetted before commencement of the works.

The Contractor is to have an Eskom certified and authorized Operating Regulation for High Voltage Systems (ORHVS) person available on site at all times in accordance with Eskom Transmission Standard Occupational Health and Safety Requirements to be met by Contractors and Sub-contractors Employed by Eskom.

The Contractor shall control his activities and processes in accordance with Eskom’s Occupational Health and Safety Requirements to be met by Contractors and Sub-contractors Employed by Eskom.

The authorization procedure for a permit to work shall be done before the contractor commences work on site.

It is the Contractors responsibility to ensure that a permit to work is obtained before access to the work can be given.

The contractor must be in possession of current H.V. Regulations and is responsible to be authorised by Western Grid GMR 2.1 and the Grid Safety Advisor to work in the region. In addition, one of his workers must have a current first aid level 2 certificates. All workers to have police clearance (no criminal record)

The contractor’s trucks must have a valid and current crane test certificate with the truck driver and crane operator’s certificate. All slings, shackles and crimping tools must have valid and current test certificates, which must be produced on site establishment.

The contractor will only leave site once a written site instruction has been issued by an Eskom site representative.

Proposed project schedule indicating man-days must be attached. Dates to be March2018onfirmed on contract award.

Working hours will be from 07h30 to 16h30 during weekdays, weekend work to be carried out only on request from Eskom.

The contractor is to provide an approved Quality Inspection and Test Plan for the design, manufacture, delivery and installation as stated in the Scope of Works.

The contractor is to provide within two weeks of contract awarding the requirements of outages for the works duration.

It is the Contractors responsibility to ensure that a permit to work is obtained before access to the site can be given. Arrangements can be made with Transmission- Central Grid, High Voltage Plant Manager.

Vehicular access to some tower sites and parts of the servitude may be restricted, prohibited or impossible and might not necessarily be linear. The Contractor is to make provision for alternative methods of construction at these positions.

### Restrictions to access on Site, roads, walkways and barricades

Access on site is restricted to the area in which the Contractor is working and which has been barricaded. Strictly no movement outside the barricaded working area unless escorted by authorized HV Plant personnel.

The majority of the work is to be performed in the live HV Yard and the contractor will take all necessary precautions and work in conjunction with Eskom personnel.

### People restrictions on Site; hours of work, conduct and records

The Contractor is to supply Eskom with Police clearance for all the employees on site before Work commences.

The normal working hours shall be from 07:30 am to 04:30 pm. Any work done outside this duration must be arranged through the senior HV Plant supervisor.

The maximum speed limit on site is 40 km/h.

### Health and safety facilities on Site

There are no Toilet facilities available on site.  The Contractor is to provide his own toilet facilities on site and ensure that these facilities are kept in a clean condition to Eskom’s satisfaction. No work on site will be allowed to commence before the toilet facilities are available on site.

### Environmental controls, fauna & flora, dealing with objects of historical interest

The Contractor shall control his activities and processes in accordance with Eskom’s Environmental Requirements TST41-120.

The Contractor shall establish a refuse control system.  All waste is to be collected and disposed of as required by Eskom and the Local Authority.

### Title to materials from demolition and excavation

All the materials from excavation and demolition must be disposed of by the Contractor except where expressly stated by the PM or the relevant staff from the Grid. All rubble and other materials must be classified, weighed and transported to a registered dumping site.

### Cooperating with and obtaining acceptance of Others

The Contractor’s attention is drawn to the fact that other contractors will be on site and access and interfacing with them will be required.  The Contractor shall allow safe access for other contractors and Eskom personnel when required.

### Publicity and progress photographs

Warning signs and notices must be clearly displayed at all sites where work is taking place. It is the responsibility of the Contractor to ensure that all its workers and visitors adhere to all signs.

No photographs are to be taken without the permission of the E.A.

### Contractor’s Equipment

All equipment must be registered in the equipment register and as per 32-136. The Contractor is responsible for his own insurance of his equipment. The Contractor is to take stock of his material and equipment on a regular basis and any shortage to be reported to the Project Manager immediately, stating if it is hired or owned.

### Equipment provided by the Employer

Not applicable

### Site services and facilities

The contractor should provide the following, drinking water, ablution facility and own accommodation. The electricity is available on site but it is not guaranteed and the contractor should make provision for that on the bill of quantities.

All the water necessary for construction purposes must be provided for by the Contractor. It is the

Contractor’s responsibility to test any water before using it for construction purposes.  The Contractor to submit a Test Certificate for the water used on site.

Electricity is available on site. The Contractor shall provide all connections, extensions and additional supply points necessary for the works. Any measures, which the Contractor may require to maintain continuity and quality of supply, shall be arranged by him at his own expense.

The Contractor shall provide everything else necessary for providing the Works.

The Contractor supplies all plant and materials required for providing the Works.

There are no Office or Telephone facilities available on site. The Contractor is to provide his own facilities on site and ensure that these facilities are kept in a clean condition to Eskom’s satisfaction.

There are no toilet facilities available on site. The Contractor is to provide his own toilet facilities on site and ensure that these facilities are kept in a clean condition to Eskom’s satisfaction. No work on site will be allowed to commence before the toilet facilities are available on site.

### Facilities provided by the Contractor

The Contractor supplies all plant and materials required for Providing the Works.

There are no Office or Telephone facilities available on site.  The Contractor is to provide his own facilities on site and ensure that these facilities are kept in a clean condition to Eskom’s satisfaction.

There are no Toilet facilities available on site.  The Contractor is to provide his own toilet facilities on site and ensure that these facilities are kept in a clean condition to Eskom’s satisfaction. No work on site will be allowed to commence before the toilet facilities are available on site.

### Existing premises, inspection of adjoining properties and checking work of Others

The Work is to be carried out inside the control room and on the HV Yard of the substation. The Contractor is to take note of the surrounding, underground piping/cables and buildings.

### Survey control and setting out of the works

The Contractor is responsible for setting out the works.

### Excavations and associated water control

All necessary precautions shall be taken to ensure that deep excavations are safe and that the sides are stable, if not they shall be battered. All excavations are to be properly barricaded at all times.

### Underground services, other existing services, cable and pipe trenches and covers

Before any excavation is commenced, it will be the responsibility of the Contractor to ascertain from the “Engineering Assistant” the position of any existing services on site.  Once these are indicated to the Contractor they shall be deemed “known”.  Any costs incurred for repairs to any “known” services shall be for the Contractor’s account.

### Control of noise, dust, water and waste

The Contractor shall control his processes and procedures so as to minimise noise and dust.  All waste is to be collected and disposed of as required by Eskom and the Local Authority.

### Giving notice of work to be covered up

The Contractor is to give the Site Supervisor at least 3 days’ notice before covering up the work

## Completion, testing, commissioning, and correction of Defects

On or before the Completion Date the Contractor shall have done everything required to complete the works, except for the work listed below, which may be done after the Completion Date, but completed before the dates stated as listed below.  The Project Manager cannot certify Completion until all the work, except for work listed below, has been done and is also free of Defects which would have, in his/her opinion, prevented the Employer from using the works and Others from doing their work.

|  | Item of work | To be completed by |
| --- | --- | --- |
|  | As built drawings | Within 14 days after Completion |

### Commissioning

Detailed commissioning procedure and compliance certificate shall be issued by the Contractor. Final certificate of compliance shall be issued by the contractor to the Employer after Completion.

### Take over procedures

Takeover is after Completion. The Employer shall require the Contractor to provide training/information session to Employer’s personnel.

### Access given by the Employer for correction of Defects

The Project Manager arranges for the Employer to allow the Contractor access to and use of a part of the works which has been taken over if needed to correct a Defect.  After the works have been put into operation, Entry to the site is governed by the Grid’s Engineering Assistant and the Contractor shall adhere to all regulations given.

### Performance tests after Completion

Requirements are specified in the xxxxxx standard, document number 240-xxxxxxxx

### Training and technology transfer

Employer requires the Contractor to provide training in the use and maintenance of the works or any associated transfer of technology from him to the Employer.

Training shall be provided for at least 10 of the Employer’s staff. 	The Employer’s preference is to have training courses conducted in South Africa wherever feasible and practical. The Employer can elect to receive the training at the Supplier’s site. Training shall be provided in the broad categories of system operations, hardware maintenance, Contractor’s software and operating system software, system implementation, maintenance and development.

Specialised hardware training courses shall include system maintenance concepts, system expansion and HMI equipment maintenance.  All hardware training shall be supplemented with periods of practical hands-on training and on-job-training. 	All software training shall be supplemented with periods of hands-on training and on-job-training.

The Contractor’s suggested approach to fulfilling the Employer's training requirements, the course descriptions, course schedules and venues, and course costs per person shall be detailed. All training material or at least the material used during the initial training shall be provided to allow the Employer to provide further training in-house. The training to be provided shall be structured to ensure compliance to the following:

- The title of each training activity shall indicate the focus which is being covered for the training;

- The purpose of each training activity shall be clearly stated.

- The specific outcomes that each training module is expected to deliver upon completion of the training module shall be clearly stated.

The methods of assessment and assessment criteria to be used for assessing the trainees on their ability to deliver on the specific outcomes shall be provided.

- The training documentation shall comply with the following layout from an information perspective:

- Clearly titled document

- Date of issue of the document (CCYY/MM/DD)

- Document review date (CCYY/MM/DD)

- Purpose of the training

- Specific outcomes, assessment methods and assessment criteria related to the training.

# Plant and Materials standards and workmanship

## Building works

Not applicable

## Civil engineering and structural works

Not applicable

## Electrical & mechanical engineering works

Requirements are specified in the xxxx standard, document number 240-xxxxxxx

## Process control and IT works

Requirements are specified in the xxxx standard, document number 240-xxxxxxx

List of drawings

## Drawings issued by the Employer

This is the list of drawings issued by the Employer at or before the Contract Date and which apply to this contract.

Note:  Some drawings may contain both Works Information and Site Information.

| Drawing number | Revision | Title |
| --- | --- | --- |
| 0.37/334 | 51 | Hydra Station Electric Diagram |
| 10.37/4025 | 4 | Hydra Optic Fibre |
| 10.18/14325 | 1 | Hydra Bay Kiosk Diagram |
| 0.37/03998 | 1 | Hydra Kiosk Layout Diagram |
| 0.37/04010 | 1 | Hydra Kiosk Layout Diagram |
| 0.37/3919 | 1 | Hydra Kiosk Connector Plates |
| Various Kiosk |  | AC/DC reticulation |

C3.2	Contractor’s Works Information

This section of the Works Information will always be contract specific depending on the nature of the works. It is most likely to be required for design and construct contracts where the tendering contractor will have proposed specifications and schedules for items of Plant and Materials and workmanship, which once accepted by the Employer prior to award of contract now become obligations of the Contractor per core clause 20.1. Typical sub headings could be a) Contractor’s design b) Plant and Materials specifications and schedules c) Other

This section could also be compiled as a separate file.

Part 4: Site Information

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C4 | Site Information |  |
|  | Total number of pages |  |

Part 4: Site Information

Core clause 11.2(16) states

“Site Information is information which

- describes the Site and its surroundings and

- is in the documents which the Contract Data states it is in.”

In Contract Data, reference has been made to this Part 4 of the contract for the location of Site Information.

Delete this note and others given in boxes like this one at final draft stage.

The compiler of this document should first consult the ECC3 Guidance Notes pages 23 and 24.  Further notes are given under each heading below.

Site Information is information about the Site at the time of tender upon which the tendering contractor bases his prices.  It is fixed and does not include anything about what happens on the Site after award; that is Works Information.

Site Information does not include weather data; that is included in the Contract Data.

If the Contractor subsequently encounters conditions which are different to those described here, he may be entitled to notify a compensation event.

# Description of the Site and its surroundings

## General description

The Hydra Substation is located in the Northern Cape Province, in the vicinity of De Aar. Coordinates for Hydra substation are -30.714612S 24.088830E; (S30 42.877  E24 5.33).  Eskom Substations are National Key points therefore all the people working on Eskom sites should be vetted before commencement of the work.

All persons requiring access to site shall notify the Project Manager two (2) weeks before such access is required. The applicant shall provide proof of identification to the Project Manager with the site access application. A permit shall be issued and all contractors/visitors are required to visibly retain the permit at all times. All contractors must attend safety training and familiarization which will be provided by the Employers safety officer before commencement of any work on site.  All contractors working at Hydra substation need to be security vetted.

## Existing buildings, structures, and plant & machinery on the Site

Work shall be restricted to the perimeter of the substation. Contractors are not allowed to enter the HV yard or any other buildings outside of the scope of works.

## Subsoil information

None

This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.

Available from Engineering Contract Strategies Tel 011 803 3008, Fax 011 803 3009