NEC3 Engineering and Construction

Short Contract (ECSC3)

| A contract between | Eskom Holdings SOC Ltd (Reg No. 2002/015527/30) |  |
| --- | --- | --- |
| and |  |  |
| for | Sasol Chem 88/11 kV Substation Breaker Room - New Cable Trench and Related Works – Detailed Specifications for Civil Works for the period of Six Months as and when required |  |
| Contents: | Compiled in accordance with CIDB Standard for Uniformity in Construction Procurement (May 2010 amendments) | Page No. |
| Part C1 | Agreements & Contract Data |  |
|  | C1.1 Form of Offer and Acceptance | [●] |
|  | C1.2 Contract Data provided by the Employer | [●] |
|  | C1.2 Contract Data provided by the Contractor | [●] |
| Part C2 | Pricing Data |  |
|  | C2.1 Pricing assumptions | [●] |
|  | C2.2 Price List | [●] |
| Part C3 | Scope of Work |  |
|  | C3.1 Works Information | [●] |
| Part C4 | Site Information | [●] |
| Documentation prepared by: | Technical Support |  |

C1 Agreements & Contract Data

# C1.1 Form of Offer and Acceptance

## Offer

The Employer, identified in the Acceptance page signature block on the next page, has solicited offers to enter into a contract for the procurement of:

Sasol Chem 88/11 kV Substation Breaker Room - New Cable Trench and Related Works – Detailed Specifications for Civil Works for the period of Six Months as and when required

The tenderer, identified in the signature block below, having examined the documents listed in the Tender Data and addenda thereto as listed in the Tender Schedules, and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the Contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data.

| The offered total of the Prices exclusive of VAT is | R[●] |
| --- | --- |
| Value Added Tax @ 15% is | R[●] |
| The offered total of the Prices inclusive of VAT is | R[●] |
| (in words) [●] |  |

This Offer may be accepted by the Employer by signing the form of Acceptance overleaf and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| For the tenderer: | (Insert name and address of organisation) |  |  |  |
| Name & signature of witness |  |  | Date |  |
| Tenderer’s CIDB registration number: |  |  |  |  |

## Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an Agreement between the Employer and the tenderer upon the terms and conditions contained in this Agreement and in the Contract that is the subject of this Agreement.

The terms of the Contract, are contained in:

Part 1	Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part 2	Pricing Data

Part 3	Scope of Work: Works Information

Part 4	Site Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule, which must be signed by the duly authorised representative(s) for both parties.

The tenderer shall within one week of receiving a completed copy of this Agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this Agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this Agreement.

Notwithstanding anything contained herein, this Agreement comes into effect on the date when the tenderer receives one fully completed and signed copy of this document, including the Schedule of Deviations (if any) together with all the terms of the contract as listed above.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| for the Employer | (Insert name and address of organisation) |  |  |  |
| Name & signature of witness |  |  | Date |  |

Note: 	If a tenderer wishes to submit alternative tender offers, further copies of this document may be used for that purpose, duly endorsed, ‘Alternative Tender No. _____ ‘

## Schedule of Deviations

Note:

- To be completed by the Employer prior to award of contract.  This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.

- The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

- A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

| No. | Subject | Details |
| --- | --- | --- |
| 1 | [●] | [●] |
| 2 | [●] | [●] |
| 3 | [●] | [●] |
| 4 | [●] | [●] |
| 5 | [●] | [●] |
| 6 | [●] | [●] |
| 7 | [●] | [●] |

By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement.

|  | #### For the tenderer: |  | #### For the Employer |
| --- | --- | --- | --- |
| Signature |  |  |  |
| Name |  |  |  |
| Capacity |  |  |  |
| On behalf of | (Insert name and address of organisation) |  | (Insert name and address of organisation) |
| Name & signature of witness |  |  |  |
| Date |  |  |  |

# C1.2 Contract Data

## Data provided by the Employer

[Instructions to the contract compiler:  (delete these two notes in the final draft of a contract)

- Please read the relevant clauses in the NEC3 Engineering and Construction Short Contract (April 2013) (ECSC3) before you enter data.  The number of the principal clause is shown for most statements however other clauses may also use the same data.

- Where the following symbol is used “[●]” - data is required to be inserted.]

Completion of the data in full is essential to create a complete contract.

| ## Clause |  |  | ## Statement |  | ## Data |
| --- | --- | --- | --- | --- | --- |
|  |  |  | ## General |  |  |
| 10.1 |  |  | The Employer is (Name): |  | Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state owned company incorporated in terms of the company laws of the Republic of South Africa |
|  |  |  | Address |  | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |
| 10.1 & 14.4 |  |  | The Employer’s representative to whom the Employer in terms of clause 14.4 delegates his actions is (Name): |  | [●] |
|  |  |  | Address |  | [●] |
|  |  |  | Tel No. |  | [●] |
|  |  |  | Fax No. |  | [●] |
|  |  |  | E-mail address |  | [●] |
| 11.2(11) |  |  | The works are |  | Sasol Chem 88/11 kV Substation Breaker Room - New Cable Trench and Related Works – Detailed Specifications for Civil Works for the period of Six Months as and when required |
| 11.2(13) |  |  | The Works Information is in |  | the document called ‘Works Information’ in Part 3 of this contract. |
| 11.2(12) |  |  | The Site Information is in |  | the document called ‘Site Information’ in Part 4 of this contract. |
| 11.2(12) |  |  | The site is |  | Sasol Chem Substation |
| 30.1 |  |  | The starting date is. |  | [●] |
| 11.2(2) |  |  | The completion date is. |  | [●]. |
| 13.2 |  |  | The period for reply is |  | [●] weeks |
| 40 |  |  | The defects date is |  | [●] weeks after Completion |
| 41.3 |  |  | The defect correction period is |  | [●] weeks |
| 50.1 |  |  | The assessment day is the |  | [●] of each month. |
| 50.5 |  |  | The delay damages are |  | [●] per day |
| 50.6 |  |  | The retention is |  | [●]% |
| 51.2 |  |  | The interest rate on late payment is |  | [●]% [Insert a rate only if a rate less than 0.5% per week of delay has been agreed] |
| 80.1 |  |  | The Contractor is not liable to the Employer for loss of or damage to the Employer’s property in excess of |  | the amount of the deductibles relevant to the event |
|  |  |  | Does the United Kingdom Housing Grants, Construction and Regeneration Act (1996) apply? |  | No |
| 93.1 |  |  | The Adjudicator is |  | the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him. (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA). |
|  |  |  | Address |  | [●] |
|  |  |  | Tel No. |  | [●] |
|  |  |  | Fax No. |  | [●] |
|  |  |  | e-mail |  | [●] |
| 93.2(2) |  |  | The Adjudicator nominating body is: |  | the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the London Institution of Civil Engineers. (See www.ice-sa.org.za ) or its successor body |
| 93.4 |  |  | The tribunal is: |  | arbitration. |
|  |  |  | The arbitration procedure is |  | the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body. |
|  |  |  | The place where arbitration is to be held is |  | [●] South Africa |
|  |  |  | The person or organisation who will choose an arbitrator - if the Parties cannot agree a choice or - if the arbitration procedure does not state who selects an arbitrator, is |  | the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body. |
|  |  |  | The conditions of contract are the NEC3 Engineering and Construction Short Contract (April 2013) and the following additional conditions Z1 to Z11 which always apply: |  |  |
| Z1 |  | Cession delegation and assignment |  |  |  |
| Z1.1 |  | The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer. |  |  |  |
| Z1.2 |  | Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. |  |  |  |
| Z2 |  |  | Change of Broad Based Black Economic Empowerment (B-BBEE) status |  |  |
| Z2.1 |  |  | Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change. |  |  |
| Z2.2 |  |  | The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Employer within thirty days of the notification or as otherwise instructed by the Employer. |  |  |
| Z2.3 |  |  | Where, as a result, the Contractor’s B-BBEE status has decreased since the starting date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Works. |  |  |
| Z2.4 |  |  | Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are those stated in Clause 91.1 and the amount due on termination includes amounts listed in Clause 92.1 less a deduction of the forecast additional cost to the Employer of completing the works. |  |  |
| Z3 |  | Confidentiality |  |  |  |
| Z3.1 |  | The Contractor does not disclose or make any information arising from or in connection with this contract available to others except where required by this contract. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time). Should the Contractor disclose information to others where required by this contract the Contractor ensures that the provisions of this clause are complied with by the recipient. |  |  |  |
| Z3.2 |  | If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Employer. |  |  |  |
| Z3.3 |  | In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure. In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed. |  |  |  |
| Z3.4 |  | The taking of images (whether photographs, video footage or otherwise) of the works or any portion thereof, in the course of Providing the Works and after Completion, requires the prior written consent of the Employer. All rights in and to all such images vests exclusively in the Employer. |  |  |  |
| Z3.5 |  | The Contractor ensures that all his subcontractors abide by the undertakings in this clause. |  |  |  |
| Z4 |  | Waiver and estoppel: Add to clause 12.2: |  |  |  |
| Z4.1 |  | Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties or their delegates or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing. |  |  |  |
| Z5 |  |  | Health, safety and the environment |  |  |
| Z5.1 |  |  | The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the works. Without limitation the Contractor: - accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Site; - warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of works; and - undertakes, in and about the execution of the works, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |
| Z5.2 |  |  | The Contractor, in and about the execution of the works, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |
| Z6 |  | Provision of a Tax Invoice and interest. Add to clause 50 |  |  |  |
| Z6.1 |  | The Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Works Information, showing the correctly assessed amount due for payment. |  |  |  |
| Z6.2 |  | If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice. Interest due by the Employer in terms of clause 51.2 is then calculated from the delayed date by when payment is to be made. |  |  |  |
| Z6.3 |  | The Contractor is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment. |  |  |  |
| Z7 |  | Notifying compensation events |  |  |  |
| Z7.1 |  | Delete from the last sentence in clause 61.1, “unless the event arises from an instruction of the Employer.” |  |  |  |
| Z8 |  | Employer’s limitation of liability; Add to clause 80.1 |  |  |  |
| Z8.1 |  | The Employer liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand). |  |  |  |
| Z9 |  | Termination: Add to clause 90.2, after the words "or its equivalent": |  |  |  |
| Z9.1 |  | or had a business rescue order granted against it. |  |  |  |
| Z10 |  | Addition to Clause 50.5 |  |  |  |
| Z10.1 |  | If the amount due for the Contractor’s payment of delay damages reaches the limits stated in this Contract Data (if any), the Employer may terminate the Contractor’s obligation to Provide the Works. |  |  |  |
|  |  | If the Employer terminates in terms of this clause, the procedures on termination are those stated in Clause 91.1 and the amount due on termination includes amounts listed in Clause 92.1 less a deduction of the forecast additional cost to the Employer of completing the works. |  |  |  |
| Z11 | Ethics |  |  |  |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |  |  |  |
| Affected Party |  |  |  | means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subconsultants or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends, |  |
| Coercive Action |  |  |  | means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally, |  |
| Collusive Action |  |  |  | means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally, |  |
| Committing Party |  |  |  | means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractors or the Subcontractor’s employees, |  |
| Corrupt Action |  |  |  | means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party, |  |
| Fraudulent Action |  |  |  | means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation, |  |
| Obstructive Action |  |  |  | means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and |  |
| Prohibited Action |  |  |  | means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action. |  |
| Z11.1 | A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof. |  |  |  |  |
| Z11.2 | The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason. |  |  |  |  |
| Z11.3 | If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2. |  |  |  |  |
| Z11.4 | A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation. |  |  |  |  |

Z12		Insurance

Z _12.1	Replace core clause 82 with the following:

| Insurance cover | 82 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 82.1 | When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force. |  |  |  |
|  | 82.2 | The Contractor provides the insurances stated in the Insurance Table A, from the starting date until the earlier of Completion and the date of the termination certificate. |  |  |  |
|  |  |  | INSURANCE TABLE A Insurance against; Minimum amount of cover or minimum limit of indemnity; Cover provided until. Loss of or damage to the works; The replacement cost where not covered by the Employer’s insurance The Employer’s policy deductible as at contract date, where covered by the Employer’s insurance; The Employer’s certificate of Completion has been issued. Loss of or damage to Equipment, Plant and Materials; The replacement cost where not covered by the Employer’s insurance The Employer’s policy deductible as at contract date, where covered by the Employer’s insurance; The Defects Certificate has been issued. The Contractor’s liability for loss of or damage to property (except the works, Plant and Materials and Equipment) and for bodily injury to or death of a person (not an employee of the Contractor) arising from or in connection with the Contractor’s Providing the Works; Loss of or damage to property Employer’s property The replacement cost where not covered by the Employer’s insurance The Employer’s policy deductible as at contract date were covered by the Employer’s insurance Other property The replacement cost Bodily injury to or death of a person The amount required by the applicable law. Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract; The amount required by the applicable law.. |  |
|  | 82.3 |  | The Employer provides the insurances as stated in the Insurance Table B - INSURANCE TABLE B Insurance against or name of policy; Minimum amount of cover or minimum limit of indemnity. Assets All Risk; Per the insurance policy document. Contract Works insurance; Per the insurance policy document. Environmental Liability; Per the insurance policy document. General and Public Liability; Per the insurance policy document. Transportation (Marine); Per the insurance policy document. Motor Fleet and Mobile Plant; Per the insurance policy document. Terrorism; Per the insurance policy document. Cyber Liability; Per the insurance policy document. Nuclear Material Damage and Business Interruption; Per the insurance policy document. Nuclear Material Damage Terrorism; Per the insurance policy document.. |  |

| Z13 | Nuclear Liability |  |
| --- | --- | --- |
| Z13.1 | The Employer is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa and is the holder of a nuclear licence in respect of the KNPS. |  |
| Z13.2 | The Employer is solely responsible for and indemnifies the Contractor or any other person against any and all liabilities which the Contractor or any person may incur arising out of or resulting from nuclear damage, as defined in Act 47 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Contractor or any other person or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer. |  |
| Z13.3 | Subject to clause Z13.4 below, the Employer waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Contractor or any other person, or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer. |  |
| Z13.4 | The Employer does not waive its rights provided for in section 30 (7) of Act 47 of 1999, or any replacement section dealing with the same subject matter. |  |
| Z13.5 | The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned. |  |
| Z14 | Asbestos |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |
| AAIA |  | means approved asbestos inspection authority. |
| ACM |  | means asbestos containing materials. |
| AL |  | means action level, i.e., a level of 50% of the OEL, i.e., 0.1 regulated asbestos fibres per ml of air measured over a 4-hour period. The value at which proactive actions is required in order to control asbestos exposure to prevent exceeding the OEL. |
| Ambient Air |  | means bbreathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet. |
| Compliance Monitoring |  | means ccompliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |
| OEL |  | means ooccupational exposure limit. |
| Parallel Measurements |  | means mmeasurements performed in parallel, yet separately, to existing measurements to verify validity of results. |
| Safe Levels |  | means airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |
| Standard |  | means the Employer’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles. |
| SANAS |  | means the South African National Accreditation System. |
| TWA |  | means the average exposure, within a given workplace, to airborne asbestos fibres, normalised to the baseline of a 4-hour continuous period, also applicable to short term exposures, i.e. 10-minute TWA. |
| Z14.1 | The Employer ensures that the Ambient Air in the area where the Contractor will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational Health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short-term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10-minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM. |  |
| Z14.2 | Upon written request by the Contractor, the Employer certifies that these conditions prevail. All measurements and reporting are affected by an independent, competent, and certified occupational hygiene inspection body, i.e., a SANAS accredited and Department of Employment and Labour approved AAIA. The Contractor may perform Parallel Measurements and related control measures at the Contractor’s expense. For the purposes of compliance, the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z14.1. Control measures conform to the requirements stipulated in the AAIA-approved asbestos work plan. |  |
| Z14.3 | The Employer manages asbestos and ACM according to the Standard. |  |
| Z14.4 | In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented, and relevant air monitoring conducted in order to declare the area safe. |  |
| Z14.5 | The Contractor’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable. |  |
| Z14.6 | The Contractor continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations, 2001. |  |
| Z14.7 | Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos contractor, instructed by the Employer at the Employer’s expense, and conducted in line with South African legislation. |  |

## Data provided by the Contractor (the Contractor’s Offer)

The tendering contractor is advised to read both the NEC3 Engineering and Construction Short Contract (April 2013) and the relevant parts of its Guidance Notes (ECSC3-GN) in order to understand the implications of this Data which the tenderer is required to complete.  An example of the completed Data is provided on page 31 of the ECSC3 April 2013 Guidance Notes.

Completion of the data in full is essential to create a complete contract.

| 10.1 | The Contractor is (Name): | [●] |
| --- | --- | --- |
|  | Address | [●] |
|  | Tel No. | [●] |
|  | Fax No. | [●] |
|  | E-mail address | [●] |
| 63.2 | The percentage for overheads and profit added to the Defined Cost for people is | [●]% |
| 63.2 | The percentage for overheads and profit added to other Defined Cost is | [●]% |
| 11.2(9) | The Price List is in | the document called ‘Price List’ in Part 2 of this contract. |
| 11.2(10) | The offered total of the Prices is [Enter the total of the Prices from the Price List]: | R[●] excluding VAT [in words] [●] excluding VAT |

C2 Pricing Data

# C2.1 Pricing assumptions

Entries in the first four columns in the Price List are made either by the Employer or the tendering contractor

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tenderer enters the amount in the Price column only; the Unit, Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for the item of work which is the rate for the work multiplied by the quantity completed, the tenderer enters the rate which is then multiplied by the expected quantity to produce the Price, which is also entered.

All Prices are to be shown excluding VAT unless instructed otherwise by the Employer in Tender Data or in an instruction the Employer has given before the tenderer enters his Prices.

If there is insufficient space in the Price List which follows, state in which document the Price List is contained.

# C2.2 Price List

The Price List is as follows / contained in _______________ (delete the text which does not apply and this note)

| Item no. | Description | Unit | Quantity | Rate | Price |
| --- | --- | --- | --- | --- | --- |
|  | The total of the Prices (excluding VAT): |  |  |  |  |

C3:  Scope of Work

# C3.1 Works Information

Sasol Chem 88/11 kV Substation Breaker Room - New Cable Trench and Related Works – Detailed Specifications for Civil Works for the period of Six Months as and when required

Description of the works

Substation Breaker Room:

The building on which the works are to be constructed is the building located adjacent to Transformer Bay 2A. The works to be constructed shall include the following: The existing floor and existing cable trenches shall completely be demolished. The existing window frames shall also be removed and disposed of. The area below the existing floor shall be excavated to the required levels as per the detailed drawing. The insitu base of the excavation shall be level and compacted to 90% of modified AASHTO density. The foundations on the substation side of the existing breaker room shall be exposed. The position of the new cable entry culverts shall be determined as per the detailed drawings. A concrete lintel shall be installed in the building walls above the top of the culverts. The necessary building props, capable of withstanding the imposed loads, shall be installed and the sections of the existing foundations cut and removed. The foundation sections which need to be removed shall be cut using a suitable concrete cutter, at dimensions wider than the culvert to and precast culvert base slab overall dimensions to provide the required workspace. The excavation for the precast culvert base slab, shall be 75mm lower than on the drawings and backfilled with fine selected granular material as per SANS 1200LE. The culvert shall extend into the new cable trench and shall be cast into the walls of the new cable trench. All spaces between the new culverts and the existing building foundations and the building walls shall be filled with 15 MPa concrete. A damp-proof membrane shall be placed below the new concrete cable trench and floor prior to casting. Steel formwork, with a smooth surface finish, shall be used to cast the new concrete cable trench using 25MPa concrete. The new cable trench shall be to the dimensions as detailed in the drawings. The required steel reinforcing shall be placed as per the detailed drawings using the required spacers to ensure stability and to maintain the required minimum concrete cover. The required supports for the breaker panel base frames shall be constructed / cast as per the dimensions on the detailed drawings. Space for two additional base frames has been provided on either side of the breaker panels. This is to make provision for access space to the cable trench below the newly installed breaker panels. The additional base frames shall need to be manufactured and supplied by the Contractor as per the detailed drawing with additional checker plates installed to cover any openings in the standard base fame. The new breaker room floor shall be cast using 30MPa as per the detailed drawings and shall be level in all directions with a high degree of accuracy due to the requirements of the MV breakers. The floor shall have a cementitious floor hardener applied the new floor as per the requirements of the manufacturer. The completed floor shall be painted with a heavy industrial wearing floor paint as soon as working the breaker room has been completed.

The widows which have been removed shall be closed using masonry brick with the same wall construction as that of the existing building. The newly placed bricks shall be plastered, primed and the entire room re-painted.

A 152 x 89 x 16 structural steel I-Beam shall be built into the existing walls just below the ceiling level. The I-beam shall run for the entire length of the building as per the drawings. From this I-beam a new ladder type cable rack shall be suspended. The cable ladder shall be suspended from the I-beam with a 50 x 50 x 5 angle iron bracket. The ladder shall also be supported by a 50 x 50 x 5 angle iron below the cable ladder. The two angle irons shall be suspended by means of a M12 threaded rod. Refer to the detail drawings for more details. The top angle iron shall be welded to the top of the I-beam prior to installation and painting. The I-beam and angle iron support brackets shall be installed below the ceiling level.

A masonry cable duct shall be constructed on the outside of the building where the control cable shall enter and exit the building. The cable duct shall be constructed complete with wooden frame and fibre cement covers as per D-DT-5239 Sheet 04.

The existing cable trenches in the substation yard shall be extended adjacent to the opening of the furthest cable entry culvert. The cable trench shall be constructed, complete as per drawing D-FS-887 Sheet 1, Detail 1, 3 and 5. The cable trench shall be tied-in with a mass concrete trench to the culvert opening below ground.

A complete electrical installation in the building shall be required with four light fittings inside the building and two external light fittings at each access door. Three plug socket outlets shall also be installed. The required sub-distribution board with the required circuit breakers shall also be installed.

C3.1.2 Work to be performed by the Contractor of the Works

a) Scope of Works

The Contractor shall completely construct the following works at Sasol Chem substation:

i) Demolition and disposal of the existing breaker room floor.

ii) Excavation, compaction, and casting of new concrete cable trench.

iii) Excavation and installation for new cable entry culverts.

iv) Construction of new 30MPa Concrete floor.

v) Installation of new I-Beam, cable rack support brackets and ladder type cable rack.

vi) Removal and disposal of the existing breaker room windows.

vii) Closing of widow openings with masonry construction, plastering and painting.

viii) Construction of masonry cable duct o the building exterior.

ix) Electrical and lighting installation for the existing relay room.

x) Construction of cable trenches in the substation yard.

The Works shall be executed in total, to Employer’s requirements, as per designs and in accordance with the relevant specifications and Employer standards

C3.1.3 Preliminary, General Costs and Site Establishment

a) Fixed Charge Items for Site Establishment

i) Site Camp

The Contractor will be responsible to locate a suitable site to establish a construction camp, site office and stores.

ii) Contractor’s Yard Fencing

The cost to the Contractor to make provision for and to erect, alter as necessary, maintain, remove and make good on completion of the works suitable fencing with access gates, etc. As necessary for the enclosure of the Contractor's yard, all to the satisfaction of the Employer's appointed Supervisor / Representative. If other suitable and safe storage facilities have already been provided, this item need not be priced.

iii) Contractor’s insurance (insurance payments, provide certificates)

The cost to the Contractor to make provision to pay all deductibles (excesses) for the risks that he may encounter during the execution of the Works, further explained in the Contract document.

iv) Site Offices (establish & maintain)

The Contractor provides a secure and accessible area for the Site Camp, which includes secure storage facilities and areas, etc. The location of the site camp shall be determined on site in consultation with the Project Manager, local communities, and the relevant authorities.

On completion of the contract, the Contractor removes the site camp and offices, and the area will be left in its original state to the satisfaction of the Employer’s Representative.

v) Site Office

• The Contractor shall provide on Site a minimum of one well illuminated, insulated furnished and ventilated site office for utilisation by the Employer / Project Manager or their Representatives. This site office shall have min. the following:

• A Suitable water supply and sanitary facilities (chemical toilet).

• First aid facilities

• Telecommunication facilities (downloading of electronic communications and printing of it)

• Access to Employers website to download latest information.

• 1 x Table, 6 x chairs and drawing/filling cabinet.

• Site dairy

vi) Site Stores (establish & maintain for safe keeping of the materials) - Material Storage Area and Store

• The Contractor shall provide a secure fenced-in yard for the whole of the contract period. Storage facilities must be of such a nature that all the Contractors materials, including Materials supplied by the Employer, are safe from theft, fire hazards and vandalism and against damage due to wind, weather. Fire breaks around the storage area, and fire-fighting equipment must be in accordance with the OHS Act, and of sufficient capacity to ensure the security of stored materials as per specifications specified elsewhere above.

• The Contractor shall provide a qualified storeman to receive and issue materials. This storeman shall maintain a proper administrative record reflecting all materials received and issued as described elsewhere in this document.

• The Contractor shall implement a materials management system on the “Kardex Method”. The method can be implemented using any equivalent materials management system available. The system shall be such that it utilises best practice principles and methods. This system will be updated continuously for monthly inspections by the Employer or his Representatives. At any time, it must be possible for the Employer to establish from these records exactly what material and/or plant is kept in store or has been erected. These figures will regularly be compared to the actual quantities measured on site and the formal Employer’s issuing invoices.

vii) Accommodation of Employees

The cost to the Contractor to make provision for accommodation for his employees that are working on a site which is not close to their home base for an extended period.

viii) Contractor's Plant, Equipment & Tools (establish, maintain and remove)

The cost to the Contractor to make provision for the necessary Plant, Equipment and Tools for the execution of the Works, maintain it in a proper and safe working condition and remove on Completion.

ix) Sanitary Facilities

The cost to the Contractor to make provision for and maintain in a thoroughly clean and tidy condition and remove on completion of the Works, proper toilets for the use of the workmen

x) Water Supplies

The cost to the Contractor to make provision for all water necessary for the execution of the Works, including all temporary plumbing, removing same and making good on completion of the Works. Potable drinking water should also be made available for the workmen.

xi) Electricity Supplies

The cost to the Contractor to make provision for all electricity and artificial lighting necessary for the execution of the Works, including all temporary installation work, removing same and making good on completion of the Works.

xii) Communications (telephones, e-mail, faxes)

The cost to the Contractor to make provision and to maintain a proper telephone or cell phone communication system as well as an e-mail and or a fax facility until completion of the Works

xiii) Security (24 hours)

The cost to the Contractor to make provision for all appropriate measures for the general security of the Works.

xiv) Setting out the Works.

Cost to the Contractor to provide templates, jigs, instruments (dumpy levels) etc. and to set out lines and levels for excavations, concrete plinths, buildings, structures, fencing, drainage, etc.

xv) Management & Programme for the works (appointment of a Supervisor)

The cost to the Contractor to make provision for the employment of a competent supervisor to supervise and manage the execution of the Works as well as to prepare a detailed programme and supporting documentation for the execution of the contract including the work of all approved Sub-Contractors engaged by Employer, representing the information that is required by the Works Information in sufficient detail to enable the Employer's Representative to assess the progress of the works at all times in comparison with the programme.

C3.2 Health & Safety (OHS Act, Construction Regulations and Eskom Safety Specifications)

C3.2.1 General

a) Personal protective equipment:

The cost to the Contractor to make provision to replace PPE. Only when required and not to purchase new PPE for each project. Only the PPE required for the risks exposed to during the Contract period should be priced. Typical PPE (Hard hats, Safety goggles or shields, Respirators, Gloves, Safety shoes, Overalls, Fall Arrest Systems, Testing of equipment.

b) Compliance with safety plan & safety file

The cost to the Contractor to make provision to comply with the list of requirements to draw up a H & S plan for the project and compile and maintain a H & S File.

c) Health & Safety Training

The cost to the Contractor to make provision for H&S training as well as the cost of the idle (unproductive) time of his employees whilst undergoing H & S training.

d) Legal appointments in terms of the OHS Act and Regulations

The cost to the Contractor to make provision for the appointees in terms of the OHS Act and Regulations I. e., qualified first aider, construction site Health and safety officer, incident / Accident investigator, if not part of the construction teams of the Contractor, and appointed full time for this purpose. The additional cost of their employment which cannot be recovered through contract rates should be allowed here.

e) Other Health and Safety items deemed necessary to comply to OHS Act, Regulations and Eskom Safety specifications.

The cost to the Contractor to make provision for the cost to comply to any other requirement of the OHS Act, i.e., to notify the Department of Labour of the Construction project, time and cost to do and record daily Risk assessments, taking responsibility of Sub-Contractors' compliance in terms of the OHS Act (Safety Plan and File), constant updating of the Health and Safety File, etc.

f) Provision of Standards and Specifications

The cost to the Contractor to obtain Standards and Specifications that are referred to in this Contract document but are not supplied in hard copy format by Eskom.

g) Special transport of workers to, at and from site i. t. o. OHS Act.

The cost to the Contractor to provide safe transport to his employees at, to and from the construction site in terms of the Construction Regulations Clause 23 (2).

C3.3 Environmental Management

C3.3.1 Compliance with environmental legislation as well as environmental specifications included in or referred to in this document.

The cost to the Contractor to all the required obtain permits should it become necessary to cut a protected tree, ensure that waste is disposed of on a permitted, legal waste site and all relevant costs payable to dumping site.

C3.3.2 General

a) Completion and submission of the expanded public works programme report

The cost to the Contractor to complete the report (one page) attached to this Contract document and submitted to the Project Manager upon completion of Electrification, Sub-transmission and Refurbishment projects and with each invoice for Minor Reticulation projects.

b) Provide for the repair to damaged water reticulation pipes

The projected cost to the Contractor of repairing damaged water reticulation and/or other underground services that were not indicated on drawings or which a superficial search by the Contractor, did not reveal.

c) Items deemed necessary for the completion of this Assessment Stage

Any other cost or contingency identified by the Contractor which is not covered in the Site Establishment and could have a cost implication to the Contractor. Must be specified to warrant inclusion in the Price Schedule.

d) Notes:

i) The Contractor is referred to the contract documents for the full intent and meaning of each clause or item. He shall allow opposite each clause or item herein contained whatever payments he may consider necessary for the carrying out and observance of such item.

ii) The Contractor shall price the Preliminaries and General Activities, in respect of all payments required for any item of work, risk, contingency or obligation, whatsoever that is not described in the Activity Schedule, and which is the responsibility of the Contractor under the contract.

iii) The Contractor shall, when requested by Employer, make available to Employer the detailed breakdown of each priced item in Preliminaries and General.

iv) In the event of the Contractor not pricing the items of the Preliminaries and General Activities in sufficient detail, the Employer reserves the right to exercise its own discretion in the apportionment to individual items of the total Preliminary and General prices within the contract documents

C3.4 Work and things to be supplied by the by the Contractor of the Works

C3.4.1 Material

a) The Contractor will supply, handle and install all material required for this project.

b) Any material shortages regarding Materials supplied by the Employer must be identified by the Contractor upon delivery. The Contractor will notify the Project Manager of such shortages within 24 hours of the identification of a shortage.

c) The responsibility for the insurance excess due to any form of damage or theft of materials rests with the Contractor.

C3.4.2 Equipment

The Contractor shall supply all the plant required to complete the works.

C3.4.3 Holding Points of the works

a) No construction activities will commence until the site is officially handed over by the Project Manager or his Representative to the Contractor.

b) No construction activities will commence prior to the submission of a detailed construction program and special tool calibration certificates, etc. by the Contractor.

c) The Employer’s Supervisor or Clerk of Works will have the prerogative to execute a proper inspection on the condition of all construction tools, equipment and vehicles prior to the commencement of any construction activities.

d) No granular material obtained from commercial sources shall be used prior to the Contractor submitting the required test results of the following test criteria to the Project Engineer for approval:

i) Sieve Analysis

ii) Mod. AASTO Maximum Dry Densities

iii) Atterberg Limits

iv) CBR

v) UCS (if applicable)

e) No results shall be considered valid if they are 3 months and older.

f) The Contractor shall test/check the compaction of every completed 150mm thick layer of the platform before the construction of the successive layer. The cost of the testing shall be included in the construction rates for the specific payment items. No additional costs for testing of constructed earthworks layers will be paid by the Employer. The Contractor shall ensure that testing is performed and completed prior to commencing Works on the following or subsequent layers. The Contractor shall include the required time to perform tests in their construction programme.

g) Strength concrete mix designs and test cube results for these mix designs, shall be the responsibility of the Contractor. The Contractor shall provide the proposed strength concrete mix designs and test results, which comply with the specified concrete strengths required, to the Project Engineer for acceptance prior to any concrete casting taking place on site. The Project Engineer’s acceptance shall not absolve the Contractor of any responsibility or accountability should the supplied data or concrete not meet the quality and performance criteria specified. No results shall be considered valid if they are 3 months and older.

h) All excavations, concrete shutters and steel reinforcement is to be inspected and approved by the Employers’ Supervisor /Clerk of Works prior to casting. Timeous requests for inspection shall be submitted to the Employers’ Supervisor / Clerk of Works at least five “5” days in advance of the concrete casting. This will allow ample time for rectifying any Works not in compliance with the requirements. The Contractor shall include the required time to perform tests in their construction programme.

i) The Contractor shall provide levels and cross sections for the calculation of earthworks quantities and agreement reached with the Employers’ Supervisor / Clerk of Works concerning the accuracy and adequacy of these before earthworks are started. Only these agreed cross sections shall be used for measurement. Unless otherwise specified all quantities for measurement and payment shall be determined from the authorized dimensions indicated on the drawings.

j) If the work is constructed in accordance with the authorized dimensions and within the allowable tolerances, the calculation of quantities for measurement and payment will be based on the authorized dimensions and not the actual dimensions to which the work has been constructed. Volumes are measured on the final compacted volumes only and not “loose” volumes in vehicles.

k) The Contractor shall level of all interim and final terrace or platform layers constructed. These levels shall be submitted to the Project Engineer for review and acceptance before any structure, foundation, cable trench or road can be erected or constructed on the platform, or any work can commence on the final completed layer of the platform. The data for the points must be provided in the following format e.g.:

Y co-ordinate X co-ordinate Height Description / Code

XX XXX.XX X XXX XXX.XX XXXX.XX SS

l) A detailed contour map is to be supplied in MicroStation (DGN) format with a separate XYZ-format ASCII file.

m) Additional holding points shall be agreed between the Contractor and the Employer’s Representative and shall be enforced as per the requirements of this documents and shall not nullify any of the above holding points.

n) The Contractor will be held accountable for any construction errors, defects, claims, etc. for continuing with the construction activities at the “hold point” stages without the written instructions from the Employers’ Supervisor or Clerk of Works after consultations with the Project Engineer.

The project needs an Environmental Management Plan (EMP) to which the contractor can refer to for comprehensive environmental requirements.

Attached is a clause that we inserted in the NEC before for substation works. Below are inputs that can go into the contract as to control environmental impact on this project.

Environmental requirements

C3.4.3. Holding points (Site establishment) 1. Location of site camp (Should not be close to any natural water body) 2. Permission from waste disposal facility for Eskom project waste to be disposed of at the facility (email acceptable) 3. Permission from registered burrow pit owner that gravel material to be mined there 4. Agreement between contractor and gravel supplier for supply of gravel to Eskom site.

5. Proof that burrow pit is a licenced facility.

6. Agreement between contractor and toilet supplier (If substation has a toilet or the CNC toilet will be used by contactor then CNC must give permission via email to contractor) 7. Contractor must give proof that the waste water treatment facility gave permission that the Eskom project toilet waste can be disposed of at their facility/ Agreement between toilet supplier and the waste water treatment facility that toilet waste can be disposed of at the facility.

8. Agreement between contractor and the construction water and drinking water supplier/ email proof from contractor if they are going to purchase drinking water from a store (proof of purchase must be filed) 9. All vehicles and equipment must be serviced up to date.

10. All stationary vehicles need to have drip trays available.

11. The site must have oil spill clean-up kits for the site camp and for each team working on site.

12. There must be sufficient firefighting equipment on site.

13. The contractor must have trained workers on its EMP, Emergency preparedness procedure, Waste management procedure, work method statements 14. There must be water available for dust suppression methods e.g. water spraying when ground is too dry while excavating trenches.

15. Waste storage area must be barricaded on site.

16. Storage area for hazardous material and waste must have a hard surface and have access control.

17. At least two labelled waste bins must be on site (General and Hazardous waste) 18. Dedicated smoking area must be available at the site camp.

V-AD 5.2.2.2 Burrow pits

The contractor cannot open a burrow pit without a licence from the department of mineral resources. This is a lengthy process. It is recommended that the contractor acquire the services of a gravel supplier who will obtain gravel from a licenced burrow pit.

  - Environmental requirements

    - The contractor is responsible for the overall execution of the activities required for construction and rehabilitation works according to the environmental requirements outlined in this document and those included in the table below:

| - Environmental document | - Applicability to this project (Yes or No) |
| --- | --- |
| - Environmental Authorisation (EA) | - NO |
| - Environmental Management Programme (EMPr) | - YES |
| - General water use authorisation (GA) | - NO |
| - Protected tree cutting permit | - NO |
| - Protected plant species permit | - NO |
| - Approval from Management authority for Protected areas | - NO |
| - Water use license (WUL) | - NO |
| - South African Heritage Resources agency (SAHRA) approval letter | - NO |
| - SAHRA demolition permit | - NO |
| - SAHRA artefacts relocation permit | - NO |
| - SAHRA grave exhumation and relocation permit | - NO |
| - Environmental Maintenance Management Plan (EMMP) | - NO |
| - Waste Permit | - NO |
| - Borrow pit license | - NO |
| - SAHRA permit for burial ground impacts | - NO |

    - The Contractor shall:-

      - Provide all employees with training on the Eskom Environmental Management Plan (EMP), Contractor EMP, Contractor Waste Management Plan, Contractor Environmental Emergency Preparedness Plan prior to construction.

      - Carry out at least one environmental emergency drill during construction.

      - Assign a resource for implementation and day-to-day monitoring of the Environmental Management Plan;

      - Demonstrate environmental competence by providing evidence of the companies’ environmental policy;

      - Keep an Environmental Incident Register on site, which must be regularly updated by the Contractor throughout the entire construction period.

      - Keep a Waste disposal register on site in which the disposal of waste shall be recorded tracked.

      - Keep a non-compliance register on site in which the non-compliances will be recorded and closed.

      - Keep Material Safety Data Sheets (MSDS) for all hazardous material to be used on the project.

    - Other special environmental restrictions which must be adhered to and as stipulated in the Environmental Management Plan are:-

      - The irresponsible use of welding equipment, oxy-acetylene torches and other naked flames which could result in veld fires or constitute a hazard.

      - No driving over the wetland at the gate of the farm where access road start.

      - No site camp to be established within 100 from the wetland at the gate.

      - Indiscriminate disposal of rubbish or rubble.

      - Deliberate littering of the site.

      - Spillage of potential pollutants, such as petroleum products.

      - Lighting of fires for cooking, heating or other purposes, and failure to exterminate any fires.

      - Use of any facility other than the chemical toilets provided.

      - Burning of wastes and cleared vegetation under any circumstances.

      - The use of rivers, streams, dams or any watercourses/surface water for washing purposes.

      - Entering areas outside of the demarcated construction area.

      - The presence of construction staff at the construction site outside of the designated construction times (06h00-18h00) i.e. no construction staff are allowed to overnight on site, outside of the demarcated construction camp.

    - Payment Items:

      - Use and maintenance of Environmental Incident Register ………….…….……..…………Unit: wks

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Use and maintenance of Waste Disposal Register ………….…….……..…………Unit: wks

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Waste disposal Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Compliance with environmental legislation and specifications specified in the EMP …….Unit: wks

- The unit of measure shall be the duration in weeks (wks) for ensuring compliance with all environmental legislation and specifications in accordance with the project specific Environmental Management Plan. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Provision of Environmental Management System tools on the projects, tools include:…...Unit:wks

- Minimum two labelled dust bins (General and Hazardous)

- One Oil spill kit for the site camp and one oil spill kit per team on site

- One drip tray per stationary vehicle and fuel filled equipment on site

- The unit of measure shall be each in use and maintenance on site in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Barricading tape and 1 meter poles to barricade around open holes and trenches on site…..Unit:wks

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of barricading and poles in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - All vehicles and equipment to be used on site must be serviced as per service plan……Unit:each

- The unit of measure shall be each used on site in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Hazardous waste must be disposed of at a hazardous waste disposal facility

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Dust suppression water spraying method – Water to spray, Water Spraying equipment

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - Provision and maintenance of portable chemically maintained toilet for male and females respectively on site. Toilets must be maintained once a week and proof of safe disposal must be obtained from service provider.

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - The contractor must make provision for the procurement of snake handlers and bee keeper services on the project in the event when snakes, bees or any other dangerous wildlife is encountered on site

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - The contractor must obtain written permission from the owner of a licenced landfill site to dispose of the construction general waste via letter and/ or email.

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

      - The contractor team must include or procure the services of a registered Pest Control Officer (PCO) to carry out herbicide application in line with prescriptions given in Eskom EMP, on the construction site where applicable.

- The unit of measure shall be the duration in weeks (wks) for the use and maintenance of Environmental Incident Register in accordance with 1.2.2. The rate shall include full compensation for all material, labour, transport, plant, and equipment for the duration of the project.

C3.4.4 Other limitations:

a) The Contractor shall use the private roads with the necessary respect and maintain them throughout the construction period. The costs for such maintenance shall be for the Contractor’s account.

b) The Contractor shall control his activities and processes in such a way as to ensure compliance with the specifications. He shall carry out as a minimum requirement all the tests laid down in the specifications and shall submit all the test results, timeously, to the Employer.

c) The Employer Standards, as indicated in Specifications of this document, are requirements of the Contract.

C3.5 STANDARD SPECIFICATIONS

C3.5.1 LIST OF SANS 1200 SERIES STANDARDISED SPECIFICATIONS ................................ 14

C3.5.2 VARIATION AND ADDITIONS TO STANDARDIZED SPECIFICATIONS ......................... 16

## C3.5.1	List of SANS 1200 Series Standardised Specifications

The following SANS 1200 Standardized Specification are applicable to this contract.

### (Note: These are not issued with the enquiry document copies and may be obtained from SABS, Private Bag X191, Pretoria, 001, Republic of South Africa)

| Document | Rev./issue | Title and Publisher |
| --- | --- | --- |
| CIVIL ENGINEERING CONSTRUCTION |  |  |
| SANS 1200 A | 1986 3 | Standardized specification for civil Engineering construction Section A: General |
| SANS 1200 AA | 1986 3 | Standardized specification for civil Engineering construction Section AA: General (small works) |
| SANS 1200 AB | 1986 3 | Standardized specification for civil Engineering construction Section AB: Engineer's office |
| SANS 1200 C | 1980 1 | Standardized specification for civil Engineering construction Section C: Site clearance |
| SANS 1200 D | 1988 3 | Standardized specification for civil Engineering construction Section D: Earthworks |
| SANS 1200 DA | 1988 3 | Standardized specification for civil Engineering construction Section DA: Earthworks (small works) |
| SANS 1200 DB | 1989 3 | Standardized specification for civil Engineering construction Section DB: Earthworks (pipe trenches) |
| SANS 1200 DM | 1981 1 | Standardized specification for civil Engineering construction Section DM: Earthworks (roads, sub grade) |
| SANS 1200 DK | 1996 1 | Standardized specification for civil Engineering construction Section DK: Gabions and pitching |
| SANS 1200 G | 1982 2 | Standardized specification for civil Engineering construction Section G: Concrete (Structural) |
| SANS 1200 GB | 1984 1 | Standardized specification for civil Engineering construction Section GB: Concrete (ordinary buildings) |
| SANS 1200 GE | 1984 1 | Standardized specification for civil Engineering construction Section GE: Precast concrete (structural) |
| SANS 1200 LB | 1983 2 | Standardized specification for civil Engineering construction Section LB: Bedding (pipes) |
| SANS 1200 LC | 1981 1 | Standardized specification for civil Engineering construction Section LC: Cable ducts |
| SANS 1200 LE | 1982 2 | Standardized specification for civil Engineering construction Section LE: Stormwater drainage |
| SANS 1200M | 1996 2 | Standardized specifications for civil Engineering construction Section M: Roads (general) |
| SANS 1200 ME | 1981 1 | Standardized specification for civil Engineering construction Section ME: Subbase |
| SANS 1200 MF | 1981 1 | Standardized specification for civil Engineering construction Section MF: Base |
| SANS 1200 MJ | 1984 1 | Standardized specification for civil Engineering construction Section MJ: Segmented paving |
| SANS 1200 MK | 1983 1 | Standardized specification for civil Engineering construction Section MK: Kerbing and channeling |
| GENERAL NATIONAL STANDARDS AND ACTS |  |  |
| Act no. 43 | 1983 | Conservation of Agricultural Resources Act. |
| Act no. 73 | 1989 | Environmental Conservation act. |
| Act no. 31 | 1963 | Fencing Act. |
| Act no. 122 | 1984 | Forest Act. |
| TRH14 | 1985 | Guidelines for road construction materials |
| Act no. 63 | 1970 | Mountain Catchment areas act. |

| Document | Rev./issue | Title and Publisher |
| --- | --- | --- |
| Act no. 85 | 1993 | Occupational health and safety act. |
| SAISC | 1990 | South African Steel Construction Handbook |
| NWP 3109 |  | Standard drawing practice |
| TMH1 | 1986 | Standard Methods of Testing Road Construction Materials |
| ESKOM NEW WORKS STANDARDS |  |  |
| NWS 1017 |  | Accident Prevention |
| NWS 1494 | 3 | Fire prevention and protection of Contractors and Eskom premises on Engineering sites |
| NWS 1060 |  | Injury prevention and protection |
| NWS 1814/C1 |  | Quality assurance requirements for civil and building contracts |
| NWS 1058 | 4 | Safety at construction sites: Requirements to be met by Contractors |
| ESKPVAAL7 | 2 | Environmental impact assessment procedure for Eskom |
| 34-479 | 0 | Specification for Battery rooms |
| ESKPBAAD6 |  | Environmental management policy |
| OPR 6204 |  | Eskom Operating Regulations |
| DTOS 0071 | 0 | Eskom Standard for Barricading |
| DTMG 0112 |  | Guideline for the application of herbicides for weed eradication in substations |
| DTNG 0012 |  | Guideline for the application of Herbicides for weed eradication in substations |
| ETP 023 |  | Herbicide management policy |
| EVS 005 | 1 | Quality requirements for quality related items and equipment |
| EVS 010 |  | Quality requirements for quality related services |
| D-FS-887 | 7 | Substation Civil work details |
| SCSASAAQ1 | 2 | Quality Control Process for the Checking of Distribution Substation Construction Before Handing Over for Commercial Operation. |
| SCSPVABM9 | 0 | Co-ordination of Safety on Capital Projects |
| 34-333 | 1 | Occupational Health and Safety Requirements to be met by Contractors and Sub-Contractors Employed by Eskom. |
| 34-1544 | 0 | Management of Asbestos |
| ESKPVAAG5 | 1 | Requirements for the safe processing, storing, removing and handling of asbestos containing material, equipment and articles. |
| 32-136 | 0 | Construction Safety. Health, and Environmental Management |
| 34-145 | 0 | Assessment Procedure for Authorisation |
| 34-146 | 0 | Authorisation Standard for operating on HV Systems |
|  |  | OCCUPATIONAL HEALTH AND SAFETY ACT, 1993 (ACT NO. 85 OF 1993) |
| D-DT-5240 |  | Earthing Standard |
|  |  | EMP for this project |

## C3.5.2	Variation and Additions to Standardized Specifications

Variations and additions to these are given in the following sections and the clauses are numbered to correspond with the standardized specifications clause number to which each variation or additional applies.

1.SANS 1200A: PRELIMINARY AND GENERAL	17

2.SANS 1200C: SITE CLEARANCE	22

3.SANS 1200D: EARTHWORKS	24

4.SANS 1200G: CONCRETE STRUCTURAL	33

5.SANS 1200LB: BEDDING (PIPES)	46

6.SANS 1200LE: STORMWATER DRAINAGE	47

- SANS 1200A: PRELIMINARY AND GENERAL

VA-A 2	INTERPRETATIONS

#### VA-A 2.8	ITEMS IN SCHEDULE OF QUANTITIES

VA-A 2.8.1	Principle

Add “plus overheads” after “Contractor’s profit” in the second line.

#### VA-A 2.8.2	Preliminary and General Section

Delete “general” between “all” and “risks” in the fourth line. Delete “on which the tender is based” in the fifth line and replace with “which form the contract.”

Add a new clause:

#### VA-A 3	MATERIALS

VA-A 3.1	QUALITY

Add:

The Contractor shall at his own expense provide everything required for the construction, completion and maintenance of the Works. The Contractor shall ensure that all the constituent parts of the Works are to the standard and quality elsewhere specified in these documents and shall ensure that they are suitable for the purpose intended by the Employer.

The Contractor shall be responsible for the strength and quality of all materials used, workmanship employed and for the stability of both temporary and permanent Works during construction.

Add a new clause:

#### VA-A 3.3	TRADE NAMES

All materials, fittings, finishes, etc. specified under a trade name, catalogue number or reference number are to be specified. The Project Manager’s approval shall be obtained for any departure from this specification.

#### VA-A 5	CONSTRUCTION

VA-A 5.1	SURVEY

The Contractor shall set out the works in accordance with the drawings provided. From the information provided on the drawings, the Contractor shall calculate the position or level, or both, of all intermediate points required for by him for the proper control of the works.

Any existing benchmarks must be carefully opened in order not to disturb them. All dirt and rust must be properly removed from the pegs and at least 2 coats of bitumen corrosion protective coating must be applied.

A 500mm x 500mm x 500mm 10MPa concrete collar must be cast around each peg to secure the benchmarks. Benchmark descriptions must be legible, engraved on a soft aluminium plate inserted on top of the concrete collar while the concrete is still fresh

Any disturbance to existing benchmarks must be reported to Eskom’s Land development department.

Add a new clause

#### VA-A 5.1.3	Provision of Survey Instruments (Electronic Total Station)

The Contractor shall supply and keep continuously on Site, a staff, steel tapes, ranging rods and in good working order, maintained in proper adjustment. These shall be made available to the Supervisor’s use at all reasonable times, together with two survey assistants.

#### VA-A 5.2	WATCHING, BARRICADING, LIGHTING AND TRAFFIC CROSSINGS

Add:

Every excavation which is accessible to the public, including other Contractor’s or the Employer’s personnel, or which is adjacent to public roads or thoroughfares, or whereby the safety of persons may be endangered shall be:

a) protected by a barrier or fence consisting of not less than two ropes or wires stretched at heights of 600 mm and 1 200 mm between poles or standards, of strength adequate to safely contain pedestrians and as close to the excavation as practicable: and

b) provided with red warning lights or other boundary indicators which are clearly visible at night or when visibility is poor.

#### VA-A 5.4	PROTECTION OF OVERHEAD AND UNDERGROUND SERVICES

Add:

Adequate prior notice by Eskom of the existence of any services shall be deemed sufficient to make such services “known” to the Contractor.

#### VA-A 5.6	POLLUTION

Add:

A refuse control system shall be implemented by the Contractor. All construction waste shall be collected and disposed of in designated dumps and covered with spoil, or as otherwise instructed by the Supervisor.

#### VA-A 5.7	SAFETY

Add:

Where equipment using high energy gamma radiation is operated on Site, such as soil density meters, the Contractor shall conform to the regulations prescribed by the Project Manager and the Department of Health. This shall apply to the transportation, storage and operation of the equipment including the use of personal dosimeters.

#### VA-A 5.8	ACCESS TO WORKS

Delete this clause

Add new clause

#### VA-A 5.9	SITE LEFT CLEAR

The Contractor shall be responsible for the clearing away of excess materials, debris and rubbish, arising from the construction of the Works, during the construction and maintenance periods.

On completion of the Permanent Works the Contractor shall, at his expense, remove all surplus material and equipment save that required for maintenance work, which shall be removed on completion of the whole of the Works. However, no guards or safety of persons may be removed, if such removal constitutes a reduction to the safety of persons.

#### VA-A 5.10	DIMENSIONS

Dimensions on the drawings are to be considered correct even if not drawn to scale. No dimensions shall be obtained by scaling.

#### VA-A 5.11	REFERENCE STANDARDS

The Contractor shall keep on the Site for reference purposes a master file containing copies of all the standards listed in the specifications.

#### VA-A 6	TOLERANCES

Add new clause:

#### VA-A 6.4	TOLERANCES NOT CUMULATIVE

Tolerances may vary only within the permissible deviation specified in each standard specification. Tolerances shall not be cumulative.

#### VA-A 6.5	MEASUREMENT OF WORK

Unless otherwise specified all quantities for measurement and payment shall be determined from the authorized dimensions indicated on the drawings.

If the work is constructed in accordance with the authorized dimensions and within the allowable tolerances, the calculation of quantities for measurement and payment will be based on the authorized dimensions and not the actual dimensions to which the work has been constructed.

#### VA-A 7	TESTING

VA-A 7.2	APPROVED LABORATORIES

Replace the contents of this clause with the following:

Unless otherwise specified in the relevant specification or in the project specification, the testing laboratories certified by the South African National Accreditation Systems (SANAS) or any other laboratory which the Project Engineer approves in his absolute discretion, will be deemed to be approved laboratories in which tests or design work required in terms of a specification may be carried out.

Add new clause:

#### VA-A 7.5	CONTROL TESTS

The Contractor shall carry out, at his cost, such tests as he considers necessary to satisfy himself that his work is sound. He shall also carry out such tests as have been specified and the costs therefore are deemed to be included in the rates unless specifically and separately itemized in the relevant Schedules of Quantities.

The Contractor shall submit the test results to the Supervisor without delay.

The Project Manager may order such additional tests, as he considers necessary to prove the compliance with the specification. The costs of these additional tests shall be borne:

a) by the Employer if the results of the additional tests indicate that the Works or the part of it that was subjected to the tests comply with the applicable requirements, and

b) by the Contractor if the results indicate that the Works or the said part of it do not so comply.

#### VA-A 8	MEASUREMENT AND PAYMENT

VA-A 8.2	PAYMENT

VA-A 8.2.1	Fixed and Value Related Items

Delete “in a single payment in terms of the first” and replace with “pro-rata payment in terms of each progress certificate”

#### VA-A 8.2.2	Time Related Items

Delete and replace with:

Payment for time-related items will be affected as follows only after payment for the relevant fixed charge item if any has been made.

Subject to the provisions of the SANS 1200A Clauses 8.2.3 and 8.2.4, payment of incremental amounts (calculated by the division of the remainder of the tendered sum by the number of months required to complete the site activities for which the relevant sum was tendered) will be authorized in each of the subsequent progress certificates until the sum tendered has been paid, provided that the Employer shall be entitled to amend the amount to be paid in respect of time-related items in the event of:

a) Extension of time being granted in accordance with the contract.

b) Adjustment to the time-related items in accordance with the terms of contract.

c) Delays caused by the Contractor which no extension of time will be granted under the contract.

#### VA-A 8.3.3	Other Fixed-charge Obligations

Add:

The Contractor is to take cognizance of the Environmental Management Programme Act, a copy of which is attached hereto and forms part of the contract documents. The Contractor is to allow a lump sum price which he deems sufficient to enable him to meet any costs he will encounter in the application of the various clauses of in the Environmental Management Programme, for the entire duration of the contract.

The Contractor is to also allow for compliance with all current Eskom Health and Safety requirements, procedures and legislation (Occupational Health and Safety Act.), which includes

the employment of registered safety officer/s, as well as the procurement and use on site, of all necessary Personal Protective Equipment (PPE).

#### VA-A 8.4.5	Other Time-related Obligations

Add:

The Contractor is to take cognizance of the Environmental Management Programme Act, a copy of which is attached hereto and forms part of the contract documents. The Contractor is to allow a lump sum price which he deems sufficient to enable him to meet any costs he will encounter in the application of the various clauses of in the Environmental Management Programme, for the entire duration of the contract.

The Contractor is to also allow for compliance with all current Eskom Health and Safety requirements, procedures and legislation (Occupational Health and Safety Act.), which includes the employment of registered safety officer/s, as well as the procurement and use on site, of all necessary Personal Protective Equipment (PPE).

Add new clauses:

#### VA-A 8.9	RATES	INCLUSIVE	OF	THECONTRACTOR’S OBLIGATIONS,	LIABILITIES	AND RESPONSIBILITIES

The rates and prices contained in the Preliminary and General Section of the Schedules of Quantities shall, together with the remainder of the obligations, liabilities and responsibilities whether or not they are expressly described therein.

#### VA-A 8.10	ADJUSTMENT TO PRELIMINARY AND GENERAL ITEMS

Adjustment to fixed and value related amounts will be made on the following basis only:

a) The first 15% variance to the contract value will not be subject to P&G adjustment.

b) If the final contract value varies by more than 15% in relation to the original contract value, the preliminaries shall be adjusted in proportion to the amount by which the difference exceeds 15% of the original contract value.

c) No other adjustments shall be made.

## SANS 1200C: SITE CLEARANCE

#### VA-C 3	MATERIALS

VA-C 3.1	DISPOSAL OF MATERIAL

Add:

The spoiling of materials unsuitable for construction will be strictly controlled by the Supervisor and indiscriminate dumping of waste of any description will not be permitted. The Contractor shall provide the Eskom Clerk of Works with the required dumping certificates.

All existing fences, fence posts and gates shall be removed and sold as scrap. The Project Coordinator shall be responsible for the scrapping of the fence materials.

All materials are to be disposed of within a distance of 50 km from the site unless otherwise ordered.

#### VA-C 5	CONSTRUCTION

VA-C 5.6	CONSERVATION OF TOPSOIL

Delete this clause and replace with:

VA-C 5.6.1	Before excavations begin, all trees shall be felled, cleared and grubbed.

VA-C 5.6.2	The remaining vegetation consisting of grasses and shrubs shall be mowed with a brush cutter so that the chopped vegetation can be included in the layer of topsoil to be removed.

VA-C 5.6.3	The topsoil and chopped vegetation shall be removed to a depth of at least 150 mm from the areas to be excavated and stockpiled in windrows or heaps. The stockpiles shall be stabilized by watering or other approved means. Stockpiles shall not exceed 1 000mm in height.

VA-C 5.6.4	After completion of the construction, the topsoil and chopped vegetation shall be spread over the areas required, trimmed, rolled, watered and maintained. Maintenance shall include the repair or erosion damage to the top soiled areas.

#### MEASUREMENT AND PAYMENT

VA-C 8.2	SCHEDULED ITEMS

Add:

VA-C 8.2.11	Demolish the following:

  - Existing foundation structures	Unit: no

  - Existing cable trenches	Unit: m

  - Existing curbing	Unit: m

  - Existing substation drainage system	Unit: sum

  - Existing fence post foundations	Unit: sum

  - Existing gates, all sizes	Unit no

  - Existing box and pipe culverts	Unit: m

The rate shall include full compensation for all equipment, labour, transport, and materials required to demolish, remove and dump at a register dump site within a 50km radius of the site. The relevant dumping certificates are to be provided as proof. All fence materials are to be sold off as scrap.

Add:

VA-C 8.2.12	Clearing of existing drainage systems:

- Manholes and inlet and outlet structures	Unit: m³

- Concrete lined drains	Unit: m³

- Substation oil holding dam	Unit: m³

The unit of measurement shall be the cubic meter of material excavated and removed, measured in place before excavation.

The rate shall in include full compensation of excavating the material, protecting the existing drainage structures, repairing of any damage to existing drainage items, dealing with any surface or subsurface water, disposing of the excavated material, including shaping and levelling-off piles of spoil material. The rates shall also include full compensation for all labour, equipment, transport and the dumping of spoil material at a registered dump site should dumping be required.

Add:

VA-C 8.2.13	Removal of existing fence wires/mesh/palisades:

- Existing boundary fencing - fencing wire only	Unit: m

- Existing diamond mesh fencing - mesh only	Unit: m

- Existing weld mesh fencing - weld mesh only	Unit: m

- Existing palisade fencing - palisade panels only	Unit: no

The unit of measure shall be the meter length of removed fence mesh or the number of palisade fence panels. The rate shall include full compensation for all equipment, labour, transport, and materials required to remove existing fence mesh, remove and dump at a register dump site within a 50km radius of the site or alternatively transport material to the CNC in order to be sold off as scrap. The relevant dumping certificates are to be provided as proof.

## SANS 1200D : EARTHWORKS

#### VA-D 2.3	DEFINITIONS

Restricted excavation Add:

Bulk excavations of width less than five metres shall also be classified as “restricted excavation". Add:

Commercial source: A source of material provided by the Contractor. Yard Stone: Insulation medium to be applied to substation yards.

#### VA-D 3	MATERIALS

VA-D 3.2	CLASSIFICATION FOR PLACING PURPOSES

VA-D 3.2.1	Material Suitable for Embankments or Terraces

Replace the contents of the sub-clause with the following:

#### VA-D 3.2.1.1	Specified Properties

  - Soft fill

The material shall have a CBR of not less than 3% at the relative density specified for compaction. It shall not contain stones or rock fragments in excess of 150mm maximum dimension or 2/3 of the layer thickness, whichever is the least. The PI shall not exceed 18 unless otherwise authorized by the Project Engineer.

  - Coarse fill

The fraction of the material smaller than 50mm shall conform to the requirements for soft fill. The material shall not contain stones or rock particles in 2/3 of the layer thickness.

Add:

#### VA-D 3.2.1	Material Suitable Yard Stone

Material to be used for yard stone shall be clean, hard and durable and of sizes varying between 19 mm to 32mm (maximum dimension)

#### VA-D 4	PLANT

VA-D 4.4	DETECTORS

The Contractor shall allow for the provision and use of suitable specialist equipment for the detection of underground pipes and cables –payment clauses 8.3.8.1 (a) and (b).

#### VA-D 5	CONSTRUCTION

VA-D 5.1	PRECAUTIONS

Throughout this clause the term "public" shall be deemed to include any other Contractors on Site.

#### VA-D 5.1.1	Safety

VA-D 5.1.1.1	Barricading and lighting

Delete a) and b) and substitute the following:

a) adequately protected by a barrier comprising two ropes or wires of adequate strength to safely contain pedestrians, stretched at heights of 600 mm and 1 200 mm above ground between poles or standards of adequate strength.

b) provided with red warning lights or any other boundary indicators clearly visible at night or when visibility is poor

VA-D 5.1.1.2	Safeguarding of excavations

Add:

g)	All work undertaken by the Contractor to ensure the safety of

excavations or adjacent structures shall be deemed to be included in his rates and no separate payment will be made, unless scheduled.

#### VA-D 5.1.2	Existing Services VA-D 5.1.2.3	Protection of cables

Add:

The provisions of this clause will also be applicable to pipes

The cost of all work, delays and disruption caused by protection measures required to the services shall be deemed to be included in the tendered rates and no additional payment or claim shall be considered.

#### VA-D 5.1.6	Road Traffic Control

Add:

The cost of any work undertaken by the Contractor in compliance with the requirements of this clause shall be deemed to have been included in the tender rates.

#### VA-D 5.2	METHODS AND PROCEDURES

VA-D 5.2.2	Excavation

VA-D 5.2.2.1	Excavations for general earthworks and for structures

Add:

No projection of earth or rock faces into the net concrete dimensions of any structure will be allowed

#### VA-D 5.2.2.2	Borrow pits

Add:

The Contractor will be required to open a borrow pit to obtain the selected material required for the roadworks. He shall perform sufficient tests to prove the suitability of these materials at his own expense.

Reinstatement of the borrow pit at the completion of the contract will be required, hence the return and spreading of overburden and topsoil has been separately billed.

The cost of selective excavation and management of the borrow pit is to be included in the various rates.

Haul and overhaul will not be paid.

A commercial source shall be a source of material provided by the Contractor. Where it is specified that the Contractor shall obtain material from a commercial source, the Contractor shall include in his prices for borrow to fill from commercial sources, for finding a commercial source of suitable material, for making all arrangements for procuring the material with the owner of the source, for the payment of royalties, charges and damages and, for transporting the material to site regardless of the distance involved. No payment shall be made for the removal of overburden or stockpiling at the commercial source and no extra payment for excavating in intermediate, hard or boulder material shall apply.

#### VA-D 5.2.2.3	Disposal

Add:

Surplus or unsuitable material will also be disposed of in the designated borrow pit area. On completion the surface shall be levelled to provide a smooth, free draining surface to the satisfaction of the Engineer.

#### VA-D 5.2.4.2	Topsoiling

Replace the last sentence of the paragraph with the following:

“The final thickness of topsoil after compaction shall be at least 100mm”

#### VA-D 5.2.4.3	Grass and other Vegetation

Add:

The Contractor shall consult with the Appointed Environmental Officer for a suitable mix of grass seeds to be prepared for the areas to be grassed. No grass or vegetation shall be planted until approval of the proposed seed mixture is received from the Eskom Environmental Officer.

Only fresh, certified seed shall be used and mixed in the presence of the Appointed Environmental officer following prescribed methods. Should a premixed batch of seed be supplied the exact composition of the seed shall be confirmed with the supplier prior to any grass or vegetation planting activities commence.

In addition to the seed mixture, the Contractor shall include the required fertilizers or other recognised soil improvement measures such as commercial compost. Should commercial compost be utilised, the Contractor shall ensure that the compost shall be well decayed, friable and free from any weed seeds or other undesirable materials or particles.

Where the risk of erosion is high the Contractor shall include the necessary anti-erosion compounds to bind the soil particles and prevent erosion until such time as the grass seed has germinated and has established.

a) Hydroseeding

Should grassing be done by hydroseeding, the Contractor shall ensure that the planned seed mixture is suitable for use in hydroseeding grassing methods.

The Contractor shall be solely responsible for establishing an acceptable grass cover and any approval of seed or seed mixtures intended for use by the Contractor shall not relieve the Contractor of this responsibility.

A suitable mulch shall be added to the hydroseeding mixture at an approved rate, determined by the appointed Environmental Officer.

Hydro seeding shall be carried out using an approved hydroseeding machine at an application rate prescribed by the approved Environmental Officer.

When an anti-erosion compound be required the compound shall be applied simultaneously with the hydroseeding mixture.

a) Hand Sowing of Approved Grass Seed Mixture

If approved by the appointed Environmental Officer, sowing of grass seed done by hand shall be done ensuring that the seed shall be spread uniformly over the entire surface and then lightly raked into the topsoiled areas.

#### VA-D 5.2.3.2	Embankments

Add:

At every stage in the forming of the terrace the general surface of the fill shall be maintained to the required grades and wherever possible the whole extend of the terrace in fill shall be constructed at the same time.

The Contractor will not be permitted to extend the terrace by successive end or side dumping.

The top of the terrace shall be finished to the required grades to a tolerance of ± 25mm and suitable boning rods and sight rails must be erected and used over the whole area of the cut and fill to arrive at this tolerance. Motor graders shall do this final trimming.

Before commencing any construction work on the prepared terrace, the Contractor must satisfy himself that this terrace is correct to the tolerance of ± 25mm.

The sides of the embankments and cuttings, which are to be true to line and grade, area to be trimmed to form slopes not steeper than one vertical to two horizontals, unless stated differently on the drawings. The rate of cut and fill to form terrace shall include trimming of embankments.

#### VA-D 5.2.3.2	Backfilling of trenches and backfilling or filling against structures

Throughout this clause delete "250 mm" and replace with "150 mm". Add:

Backfilling shall be compacted to 93% Mod. AASHTO dry density unless otherwise indicated on the drawings. Backfilling shall not commence until three days after the concrete has been cast.

#### VA-D 5.2.4	Finishing VA-D 5.2.4.1	Top Soiling

Add:

Topsoil brought back to form a slightly compacted layer of at least 150mm thick on terraces and slopes must be trimmed to exact line and levels indicated on drawings. This trimming should be dome mechanically.

The rate for topping certain areas with soil shall include all operations: Loading, bringing back of temporary stockpile topsoil, dumping, trimming and compaction.

#### VA-D 5.2.5	Transport for Earthworks VA-D 5.2.5.1	Freehaul

Delete and replace with:

No overhaul will be paid. All haul will be freehaul.

#### VA-D 5.2.5.2	Overhaul

Omit this clause.

#### VA-D 7	TESTING

VA-D 7.2	TAKING AND TESTING OF SAMPLES

Add:

a) Field Density Control

Density control shall be either by sand replacement or by a nuclear density meter. The use of the nuclear density meter will be subject to the following provisions:

The tests will not be valid unless the instrument is properly calibrated at the depth of test and the test performed not within 1 meter of any concrete structure or face of an excavation in a confined space of width less than 2m.

For every 10 nuclear density meter tests a minimum of 3 corresponding sand replacement tests shall be performed.

The accuracy of any nuclear density meter shall be proved to the Supervisor by performing at least twenty comparative nuclear density and sand replacement tests before the results of the nuclear density meter will be accepted as valid. Thereafter the correlation between the nuclear density meter and sand replacement tests shall be reviewed on a fortnightly basis and presented to the Supervisor.

Each nuclear density meter shall have a certificate stating that the machine is in good working

order. Each density meter shall be re- calibrated at least once a year. Certificates of proof of re- calibration will be required.

The minimum number of density control tests shall be 4 sand replacement tests or 12 nuclear density meter tests per production lot or 500 m3, whichever is less.

A production lot shall mean a portion of fill placed and compacted in one process, using material from a single zone in a borrow area. If production continues uninterrupted, a production lot will usually be taken as one day’s work and shall not exceed two days production.

The Supervisor may order a production lot of reduced quantity, if:

- the fill material being used shows variation in quality

- a low production rate is maintained.

The acceptance criteria for density test results shall be as follows:

| SPECIFIED DENSITY% MOD AASHTO | MINIMUM AVE. DENSITY (FOR NUMBER OF TESTS GIVEN BELOW) |  |  | MINIMUM VALUE OF ANY SINGLE TEST (FOR NUMBER OF TESTS GIVEN BELOW) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3&4 | 5 | 6 |  | 3&4 | 5 | 6 |
| 90 | 90.7 | 90.9 | 91.1 |  | 89.3 | 89.1 | 88.9 |
| 93 | 93.7 | 93.9 | 94.0 |  | 92.3 | 92.1 | 92.0 |
| 95 | 95.6 | 95.8 | 95.9 |  | 94.4 | 94.2 | 94.0 |

a) Maximum Dry Density (Mod AASHTO)

A minimum of one Maximum Dry Density test per production lot or per 500 m3 whichever is the minimum, shall be carried out provided that the material is obtained from one source. The production lot shall be as defined above. The Supervisor may require more tests if the material varies in quality.

b) TMH 1: Standard methods of testing road construction materials.

#### VA-D 8	MEASUREMENT AND PAYMENT

VA-D 8.1	BASIC PRINCIPLES

Add new clauses:

VA-D 8.1.4	No separate payment will be made for the selection of excavated material in excavations or in borrow areas.

VA-D 8.1.5	The rates tendered for excavation shall cover the cost of providing adequate safeguarding. No separate payment will be made for safeguarding in the form of shoring and timbering, or battering back, unless scheduled.

VA-D 8.1.6	The cost of any tests to prove the compliance of material and the placement thereof as specified shall be included in the rates unless scheduled.

VA-D 8.1.7	The excavation rates shall include for all the Contractor’s obligations and responsibilities in respect of dealing with water on the Works.

#### VA-D 8.2	COMPUTATION OF QUANTITIES

VA-D 8.2.3	Delete and replace with:

Levels and cross sections for the calculation of earthworks quantities shall be taken by the Contractor and agreement reached with the Supervisor concerning the accuracy and adequacy of these before earthworks are started. Only these agreed cross sections shall be used for measurement.

#### VA-D 8.3	SCHEDULED ITEMS VA-D 8.3.2	BULK EXCAVATION

a)	Excavate in all materials and use for embankment or backfill or dispose as ordered.

To this clause add:

Compaction of material:

(1)	To 95% of modified AASHTO maximum

dry density at ± 2% OMC	Unit: m³

The rate shall also cover the cost of selection to remove residual roots and organic material and spoiling of these, and of compaction of the material.

b) Excavate in all materials and place on stockpile	Unit: m³

The rate shall cover the cost of complying with all precautions required in terms of 5.1 in addition to the cost of excavation in all materials, selection to remove residual roots and other organic material and spoiling of these, loading, all haul, offloading, spreading and the maintaining the stockpile.

c) Excavate in all materials and spoil	Unit: m³

The rate shall cover the cost of complying with all precautions required in terms of 5.1 in addition to the cost of excavation in all materials, basic selection, loading, all haul, offloading and spreading.

VA-D 8.3.3	RESTRICTED EXCAVATION

a) Excavate for restricted foundations, footings and pipe trenches in all materials and use for embankment or backfill or dispose.

Add:

b) Excavate in all materials and place on stockpile	Unit: m³

The rate shall cover the cost of complying with all precautions required in terms of 5.1 in addition to the cost of excavation in all materials, selection to remove residual roots and other organic material and spoiling of these, loading, all haul, offloading, spreading and the maintaining the stockpile.

c) Excavate in all materials and spoil	Unit: m³

The rate shall cover the cost of complying with all precautions required in terms of 5.1 in addition to the cost of excavation in all materials, basic selection, loading, all haul, offloading and spreading.

VA-D 8.3.14	Application of herbicide to substation yard prior to placing yard stone	Unit: m²

The unit of measure shall be the square meter area of yard stone to be applied with an approved herbicide.

The rate shall include full compensation for all transport, procurement of the material, labour, and equipment to mix and apply the herbicide to the substation yard stone in accordance with 240- 125477962 - Herbicide Usage in Eskom Prohibited and Restricted Areas, Live Chambers, Telecommunication Infrastructure Yards and Security Fences.

### VA-D 8.3.15	Substation Yard stone:

a) Removal of existing yard stone to required depth:

1)Remove and Place in Stockpile	Unit: m³

2) Remove and Spoil	Unit: ………………………………………………………………… m³

The unit of measure shall be the cubic meter volume (m³) of existing yard stone which is removed and stockpiled or removed and spoiled at a designated site.

The rate shall include full compensation for all equipment, labour, transport, and materials required to remove existing yard stone to stockpile for sub-item1), or to a designated spoil area/site for sub-item 2).

a) Cleaning and Re-Utilizing Existing Yard Stone Placed in Stockpile

1) Clean, Wash and Process Existing Fouled Yard Stone	Unit: m³

2)Extra-over item VA-1200D - 8.2.15 b) 1) for	Unit: m³

Stockpiling of Cleaned Yard Stone

The unit of measure shall be the cubic meter volume (m³) of existing yard stone which is cleaned / washed / processed and stockpiled separately from fouled yard stone.

The rate shall include full compensation for all equipment, labour, transport, and materials required to clean / wash / process existing fouled yard stone from existing stockpiles for sub- item 1) and stockpiling cleaned yard stone in separate stockpile areas for sub-item 2).

a) Place, spread, level to nominal depth of 100mm,	Unit: m³

and lightly roll Yard Stone

The unit of measure shall be the cubic meter volume (m³) of yard stone which to be placed to a nominal depth of 100mm, levelled and lightly rolled.

The rate shall include full compensation for all equipment, labour, transport, and materials required to load from existing stockpiles, offload on site, place, spread, level to a nominal depth of 100mm and lightly roll placed yard stone.

a) Testing and Importing of Yard Stone

1) Testing of material to determine suitability for	Unit: no use as substation Yard Stone in accordance with CIGRE SA 2015 Paper 46

The unit of measure shall be the number of tests performed in accordance with CIGRE SA 2015 Paper 46.

The rate shall include full compensation for all equipment, labour, transport, and materials required to performs tests on proposed yard stone materials in accordance with CIGRE SA 2015 Paper 46. The rate shall also in include full compensation for preparing and submitting a detailed report of the test results to the Primary Plant Engineer.

2) Extra-over item VA1200 – D - 8.3.15 c) for the Importation Unit: m³of Yard Stone from Commercial Sources

The rate shall cover the additional cost of supplying yard stone materials from commercial sources. The rate shall include all additional costs of finding a suitable source or materials, procuring the material inclusive of all royalties or other charges by the owner of the source, transportation of the material from the source to a designated stockpile on site

## SANS 1200G:	CONCRETE STRUCTURAL

#### VA-G 2	INTERPRETATIONS

VA-G 2.4	EXPLANATION OF TERMS

VA-G 2.4.2	 Strength Concrete

Add:

Where the aggregate size is not specified, the Contractor shall use a size of coarse aggregate consistent with the requirements of clause VA-G 3.4.1.

#### VA-G 3	MATERIALS

VA-G 3.1	APPROVAL OF MATERIALS

Delete and replace with:

No later than three weeks prior to the commencement of concreting, the Contractor shall supply to the PE/TAP Alliance for its approval, samples of the fine and coarse aggregates that he proposes to use for the concrete and shall demonstrate by means of a report from an approved laboratory that the aggregate comply with the requirements of SANS 1200 clause 3.4.

The Contractor shall demonstrate also by means of a report from an approved laboratory

a) All aggregates used in the concrete mix meet the requirements as per SANS 1083.

b) That the aggregates do not exhibit excessive shrinking properties, in accordance with clause C.14, Appendix C of SANS 1083.

a) That the aggregates do not have a potential for Alkali Silica reaction. In this regard a petrological examination of the aggregate and report by a qualified Geologist, shall accompany the laboratory report.

b) In accordance with the recommendations of the Cement and Concrete Association. Slough, England, Working Party Report – Minimising the Risk of Alkali-Silica Reaction. September 1983.

or

c)In accordance with the latest recommendations of the National Building Research Institute.

The Contractor shall not commence concreting until the Eskom Supervisor has approved in writing the aforesaid materials.

#### VA-G 3.2	CEMENT

VA-G 3.2.2	Alternative Types of Cement

Delete this clause and replace with:

a) Where the aggregates have been shown in terms of clause VA-G 3.1 to have no potential for Alkali Silica Reaction, concrete shall be manufactured using only the following cements or blends of cements as constituting the cementitious portion of the concrete mix.

  - Ordinary Portland Cement (OPC)

  - Portland Cement 15 (PC 15)

In such case the use of other cements or cement blends may be permitted only on the written approval of the PE/TAP Alliance.

b) Where the aggregates have been shown in terms of clause VA-G 3.1 to have a potential for Alkali-Silica Reaction the concrete shall be manufactured using:

iii)Low Alkali OPC which will fulfil the requirements of Clause VA-G 5.5.1.7 or

iv)PBFC or a 50:50 blend of OPC and Slagment or

#### VA-G 3.2.3	Storage of Cement

Add:

Cement and cementitious materials shall not be stored longer than 3 months.

Should storage of cementitious materials be longer than 3 months through reasons beyond the control of the Contractor he may have the material tested by an approved laboratory for compliance with the standard and apply to Eskom for a concession.

Cement shall also be stored in such a manner that it is handled on a “first in, first out” basis.

#### VA-G 3.4	AGGREGATES

VA-G 3.4.1	Applicable Specifications

Add:

The maximum size of coarse aggregate for structural concrete, unless stated on the relevant drawings, shall not exceed:

a) One fifth of the thickness of the concrete element.

b) 5mm less than the clear distance between reinforcing bars.

a) 40mm.

Coarse aggregate for use in mass concrete may be larger than 40mm, if not shown on the drawings or approved by Eskom.

#### VA-G 3.4.2	Use of Plums

Delete and replace with:

Plums shall not be used.

#### VA-G 3.5	ADMIXTURES

Add:

The Contractor shall stipulate the technical reasons indicating the use of admixtures in the mix. Adequate test mixes and test samples to the satisfaction of Eskom shall be prepared to demonstrate that the presence of the admixture has no detrimental effect on any of the characteristics of the fresh and hardened concrete specified elsewhere herein.

No admixtures containing chlorides shall be used.

#### VA-G 3.9	HOLDING DOWN BOLTS

All holding down bolts shall be galvanised to SANS 763 for a length of 100mm below the bottom of the thread unless otherwise indicated on the drawings.

Nuts and washers used with the HD bolts shall be galvanised to SANS 763.

#### VA-G 5	CONSTRUCTION

VA-G 5.1	REINFORCEMENT

VA-G 5.1.1	Bending

Add new clause:

#### VA-G 5.1.1.5	Reinforcement shall be cut with cropping or shearing equipment

Cutting torches shall not be used.

#### VA-G 5.1.2	Fixing

Add:

No welding of reinforcement shall be permitted.

#### VA-G 5.1.4	Splicing

Add:

Screw type or Swage type connectors or additional splice lengths from those indicated on the Drawings shall be subject to the approval of Eskom.

#### VA-G 5.2	FORMWORK

VA-G 5.2.1	Classification of Finishes

b)	Smooth

Add:

This finish shall be obtained by the use of steel-faced forms arranged in a regular pattern to fit the appearance of the structure.

Add new clause:

#### VA-G 5.2.6	Chamfers

Unless otherwise specified all exposed corners and arises shall have a 20x20mm chamfer.

#### VA-G 5.3	HOLES, CHASES AND FIXING BLOCKS

Add:

Holes or chases shall be thoroughly cleaned and prepared prior to the placing of concrete or grout. They shall be subject to approval by Eskom.

#### VA-G 5.5	CONCRETE

VA-G 5.5.1	Quality

VA-G 5.5.1.1	General

Delete the first sentence and replace with:

Only strength concrete shall be used.

#### VA-G 5.5.1.7	Strength concrete

Add:

The Contractor shall design trial mixes in accordance with SANS 10100-2, 2014. The target strength of the trial mix shall be determined using K equal to 1,7 and a standard deviation of 5 MPa for a “good” degree of site control.

Target Strength = Specified Strength + (K x standard deviation).

The Contractor shall submit the trial mixes together with 7- and 28-day test results to Eskom for approval. The average 28-day test result shall equal or exceed the target strength. No concreting shall proceed until the trial mixes have been approved.

Where it has been shown in terms of clause VA-G 3.4.1 that aggregate to be used in the Works has a potential for Alkali Silica Reaction, the concrete mixes shall be designed so as to ensure that the alkali content of the concrete calculated in accordance with clause 4.4 of the Cement and Concrete Association Working Party Report – Minimising the Risk of Alkali Silica Reaction, September 1983 – does not exceed 2,1 kg/m³.

#### VA-G 5.5.2	Batching

VA-G 5.5.2.3	Aggregates

Add:

Volume batching is permitted for concrete pours of up to 0,5m³. All greater quantities shall be weight batched to an accuracy of 2%.

#### VA-G 5.5.3	Mixing

VA-G 5.5.3.1	Mixing at construction site VA-G 5.5.3.1	b)	Add:

Where the use of cement has been approved by Eskom, the OPC shall be batched into the mixer before the addition of the other cementitious constituent.

g)	Delete and replace with:

Concrete shall only be retained in the mixer for such additional time such that the concrete is placed within one hour of the start of mixing. In such event the mixer shall not turn continuously but shall run for only 2 minutes every 15 minutes. Eskom may order that the period of one hour be reduced if in its opinion the ambient temperature or any other factor will tend to produce early setting.

Concrete thus retained shall ever so comply with all other requirements of the specification, and failure to comply shall result in the rejection of such concrete.

#### VA-G 5.5.3.2	Ready-mixed concrete

Add:

Ready-mixed concrete other than that produced at the Contractor’s own central mixing plant shall not be used without Eskom’s written consent

#### VA-G 5.5.5	Placing

VA-G 5.5.5.1	Delete and replace with:

The Contractor shall give Eskom adequate notice of his intention to place concrete.

Concrete shall be placed within one hour of the start of mixing (and not “within one hour its discharge from the mixer”). Concrete shall not be re-tempered in any way whatsoever. The forms to be filled shall be clean internally. All excavations and other surfaces of an absorbent nature that are to come into contact with the concrete shall be thoroughly dampened with water immediately prior to placing. There shall be no free water standing on the surfaces against which concrete is to be placed.

No “cold joints” resulting from any discontinuity of any pour will be permitted.

#### VA-G 5.5.6	Compaction

VA-G 5.5.6.3	This clause is amplified as follows:

Concrete shall not be compacted by spading, rodding or forking.

#### VA-G 5.5.7	Construction Joints VA-G 5.5.7.1 Add:

The Contractor shall continue concreting through meal breaks or after normal working hours in order to complete work up to a construction joint and no extra payment shall be made to the Contractor for overtime working.

VA-G 5.5.7.2	Add:

The Contractor shall continue concreting through meal breaks or after normal working hours in order to complete work up to a construction joint and no extra payment shall be made to the Contractor for overtime working.

VA-G 5.5.7.3

Add:

The finishing-off of concrete to form unforeseen joints shall be to the approval of Eskom. In the event that the position of such unforeseen joints in the opinion of Eskom jeopardises the design of the Works, Eskom shall have the right to instruct the Contractor to break down and remove all such concrete to a point to be determined by Eskom.

All costs relating to such breaking down and removal of the defective work as well as those related to the reinstatement of the Works in accordance with the contract shall be borne by the Contractor.

Add new clauses:

#### VA-G 5.5.7.4	Joint former material

Joints shall be formed using material specified on the drawings.

#### VA-G 5.5.7.5	Joint sealing

Sealing compounds shall be as indicated on the drawings.

The sealing compounds shall be supplied by a sub-Contractor approved by the Engineer.

Joints shall be prepared, primed and sealed in strict accordance with the sealant manufacturer’s requirements.

The joints to be sealed shall be formed by the Contractor to the sizes shown on the drawings.

The restoration of incorrectly constructed and/or damaged joints to the specified sizes shall be carried out using two-part epoxy mortar designed for the repair of spalled and damaged concrete which shall be applied in strict accordance with the manufacturer’s requirement

Add new clauses:

#### VA-G 5.5.7.4	Joint former material

Joints shall be formed using material specified on the drawings.

#### VA-G 5.5.7.5	Joint sealing

Sealing compounds shall be as indicated on the drawings.

The sealing compounds shall be supplied by a sub-Contractor approved by the Engineer.

Joints shall be prepared, primed and sealed in strict accordance with the sealant manufacturer’s requirements.

The joints to be sealed shall be formed by the Contractor to the sizes shown on the drawings.

The restoration of incorrectly constructed and/or damaged joints to the specified sizes shall be carried out using two-part epoxy mortar designed for the repair of spalled and damaged concrete which shall be applied in strict accordance with the manufacturer’s requirements.

#### VA-G 5.5.8	Curing and Protection

Add:

Precautions shall be taken to prevent cycles of wetting and drying.

The curing and protection of concrete is vital, and the Contractor shall comply strictly with these requirements. Blinding layers, of thickness 50mm or less, needs to be cured.

#### VA-G 5.5.10	Concrete Surfaces

VA-G 5.5.10.2	Delete and replace with:

Concrete surface finishes required will be indicated on the drawings and shall be classified as follows:

a) Rough: This shall comprise a lightly ridged surface as struck off with a tamping board. Degree of Accuracy III is required. This finish shall provide a good key for subsequent finishing with a screed or bituminous carpet.

b) Smooth wood float: The surface shall be wood floated to a uniform surface free of trowel marks and shall be Degree of Accuracy II.

c) Smooth Steel Float: The surface shall be accurately struck of and floated and finished with a steel float to a smooth and uniform surface, free of trowel marks, to degree of Accuracy.

Rubbing with a Carborundum stone will be permitted in certain circumstances but no plastering to correct imperfections will be permitted.

#### VA-G 5.5.13	Grouting

Delete and replace with:

The Contractor will be required to grout under structural steel baseplates erected by other

Contractors.

a) Surface Preparation

The concrete surface shall be scabbled and thoroughly cleaned so that all unsatisfactory material such as dust, oil, grease and laitance is removed.

The surface shall be kept wet for at least 12 hours prior to grouting but no standing water shall remain at commencement of grouting.

- Mixing

All grouting shall be done using a non-metallic, non-shrink, and proprietary grout having a minimum compressive strength at 28 days of 35 MPa. The grout shall be mixed at a “plastic” consistency to the grout suppliers’ specifications. Any mixed grout shall be discarded if not placed within 1 hour of mixing and no partially set grout may be re-tempered.

- Placing

Waterproof shutters shall be securely fixed to three sides of the baseplate and the grout forced in and tightly caulked using a wooden tamping tool. The cavity shall be slightly over- filled, and a closing shutter introduced.

In the case of obstructive levelling packs, two adjacent sides shall be shuttered, and grout placed behind the packs before the third shutter is fixed and the grouting is completed.

- Stripping and curing

Once the grout has reached an initial set, the shutters may be stripped, and a coating of curing compound be applied to all exposed grout surfaces.

- Alternative: Use of Liquid Grout

Should the Contractor so choose the grout may be mixed to a free- flowing consistency and installed by means of a headbox and tail reservoir shutter system to the grout supplier’s specifications.

#### VA-G 5.5.14	Defects

VA-G 5.5.14.2	Delete and replace with:

After thorough inspection and investigation of the quality and strength of the work, as a first priority the Contractor shall propose the extent and method of repair for Eskom’s approval. Notwithstanding the foregoing Eskom may order alternative or more extensive methods of repair or order the demolition and reconstruction of the whole of the defective element of work that it considers necessary.

The costs of all such investigation, repair and remedial work and any demolition and reconstruction work shall be borne by the Contractor and all repair, remedial and reconstruction work shall be the satisfaction of Eskom.

Add new clause:

#### VA-G 5.5.16	Holding Down Bolts

All holding down bolts and anchorages, shall be set absolutely true in accordance with the Drawings by means of accurately constructed templates and securely fixed in position to prevent displacement during concreting.

Exposed threads of holding down bolts shall be adequately protected with grease and sacking and this protection shall be maintained in all portions of the Works until they are taken over.

#### VA-G 6	TOLERANCES

VA-G 6.2	PERMISSIBLE DEVIATIONS

VA-G 6.2.3	Specified Permissible Deviations

d)	Elements or components above foundations

4)	Level (deviation from designated level with reference to the nearest transferred datum (TD) of the upper surface of any slab or other element or component.

|  | DEGREE OF ACCURACY I |  |
| --- | --- | --- |
| 7) | Delete And replace with Exposed Concrete Surface DEGREE OF ACCURACY I Flatness of Plane surface | -10mm + 0mm 4mm 3mm |
| a) | Delete and replace with: All elements except Transformer Plinths | 3mm |
| b) | Transformer Plinths | 2mm |
| ii) | Abrupt changes in a continuous surface |  |

Concrete surfaces adjacent to angle iron edgings of cable trenches shall be laid at a level such as to ensure that the surface of the specified floor covering can be laid and finished off flush with the angle irons with no abrupt changes in levels.

Permissible deviations in Degree of Accuracy I for items not specified in SANS 1200 G sub-clause

6.2.3 shall be as follows:

Concrete surfaces adjacent to angle iron edgings of cable trenches shall be laid at a level such as to ensure that the surface of the specified floor covering can be laid and finished off flush with the angle irons with no abrupt changes in levels.

Permissible deviations in Degree of Accuracy I for items not specified in SANS 1200 G sub-clause

6.2.4 shall be as follows:

Concrete surfaces adjacent to angle iron edgings of cable trenches shall be laid at a level such as to ensure that the surface of the specified floor covering can be laid and finished off flush with the angle irons with no abrupt changes in levels.

Permissible deviations in Degree of Accuracy I for items not specified in SANS 1200 G sub-clause

    - shall be as follows:

#### f) Location of holding down bolts

  - The Centerline of a holding down bolt from its designated location in plan 2mm.

  - The top of the bolt from its designated elevation 4mm.

Add new clause:

#### Location of holding down bolts

1)     The center line of a holding down bolt from its designated location in plan 2mm.

2)    The top of the bolt from its designated elevation 4mm.

Add new clause:

#### Location of built-in Items

1)From the defined positions in plan - ± 25mm.

2)From the defined position in level – in accordance with the tolerances specified for the formwork to which it is related.

Add new clause:

#### Location of built-in Items

1)  From the defined positions in plan - ± 25mm.

2) From the defined position in level – in accordance with the tolerances specified for the formwork to which it is related.

Add new clause:

#### Location of built-in Items

1)From the defined positions in plan - ± 25mm.

2)From the defined position in level – in accordance with the tolerances specified for the formwork to which it is related.

#### VA-G 7	TESTS

VA-G 7.1	FACILITIES AND FREQUENCY OF SAMPLING

VA-G 7.1.1	Facilities

Add:

The Contractor shall be fully responsible for sampling and testing the concrete at the frequency laid down.

#### VA-G 7.1.2	Frequency of Sampling

Every time a sample is taken, a slump test is to be performed on the same batch of concrete and the result recorded.

From every sample 6 cubes are to be made and 3 cubes tested at 7 days and 3 cubes tested at 28 days.

Sample shall be taken at the point of placing.

#### VA-G 8	MEASUREMENT AND      PAYMENT VA-G 8.1	MEASUREMENT AND RATES

VA-G 8.1.3	CONCRETE

VA-G 8.1.3.2	Delete and replace with:

Separate items will be scheduled, as applicable for each type and each grade of concrete.

Concrete will not be separately scheduled for the exact location in the Works; however it shall be separately scheduled for placing in different types of structural elements.

#### VA-G 8.1.3.3	a)	Delete and replace with:

The rates shall cover the cost of the design of the mix in the case of strength concrete, the provision of concrete (made with the cement type schedule or, where not scheduled, as listed in clause VA-G 3.2.2), designated joints other than expansion and contraction joints shown on the drawings, mixing, transporting, testing, placing, compacting, the forming of kickers, stop-ends and unforeseen construction joints, striking-off or levelling as applicable, and curing and repairing where necessary.

Any precautions required for mixing and batching, transporting, placing and curing in adverse weather conditions shall be covered in the rate.

Any precautions required for mixing and batching, transporting, placing and curing in adverse weather conditions shall be covered in the rate.

Add new clause:

VA-G 8.1.3.4  a)  Where  concrete  foundations  for  steel  columns,  transformers  and  equipment,  cable  trenches and junctions are scheduled in the Bill of Quantities as a Unit, or per metre of length, as applicable, the rate shall cover all the costs associated with the construction of the unit or per metre, within the dimensions of the item, in compliance with the specifications and as shown on the drawings, including excavation in soft material, disposal, blinding, concrete, reinforcement, formwork, backfilling, finishing off, curing, testing and any other items which may be required.

Extra-over payment will be made for Intermediate or Hard Rock  material encountered in the excavations.

b)	 Where concrete, reinforcement, formwork and associated items are separately scheduled clauses SANS 1200 G, 8.1.1 to 8.8 and the variations and additions to these shall apply.

#### VA-G 8.4	SCHEDULED CONCRETE ITEMS

VA-G 8.4.2	Blinding layer in ………. Concrete ……….

Delete and replace with:

Minimum Thickness and Grade

- Cast against soft excavation	Unit: m²

- Cast against intermediate excavation	Unit: m²

- Cast against hard rock excavation	Unit: m²

#### VA-G 8.7	GROUTING

Amend the unit of measurement to litre (dm3) in sub-clauses (a) and (b).

a)	Under bases (or beds).

Add:

The rates for grouting under bases or beds shall include the cost of any shuttering required.

#### VA-G 8.9	Construction of transformer plinth complete with Bund wall and drainage system as indicated:

- Normal entrance:

  - 5 – 20 MVA D-DT-5231 sheet 1	Unit: no

  - 20 – 40 MVA D-DT-5232 sheet 1	Unit: no

  - 40 – 80 MVA D-DT-5236 sheet 1	Unit: no

- Side entrance:

  - 5 – 20 MVA D-DT-5231 sheet 2	Unit: no

  - 20 – 40 MVA D-DT-5232 sheet 2	Unit: no

  - 40 – 80 MVA D-DT-5236 sheet 2	Unit: no

The unit of measure shall be number of transformer plinths and bundwalls constructed complete as indicated on the drawings.

The rate shall include full compensation for transport, procurement, safe keeping of the all the material required, setting out, shuttering, all excavations, confirming of construction levels, labour, and equipment for the complete construction of the foundations.

#### VA-G 8.10	Construction of cable trench complete indicated:

- Single type A cable trench D-FS-887 sheet 1	Unit: m

- Double type A cable trench D-FS-887 sheet 1	Unit: m

- Precast concrete trench cover with support

steel work D-FS-887 sheet 1	Unit: m

- Single cable trench under road D-FS-887 sheet 1	Unit: m

The unit of measure shall be a linear meter of cable trench constructed with cable trench bends, support steelwork, cable trench covers.

The rate shall include full compensation for all transport, procurement and safe keeping of the all the material required, all excavations required, setting out of trenches, confirming of construction levels, labour, and equipment for complete construction of the cable trench.

VA-G 8.11	Repair of existing Oil Dam Walls and reinstating fill

- Repairing of walls	Unit: m²

- Reinstating of fill	Unit: m³

- Clearing of debris in oil dam	Unit: m³

The unit of measure for sub-item (a) shall be the square meter area of wall to be repaired in accordance to detailed drawings D-DT-5234.

The unit of measure for sub-item (b) shall be the cubic volume of fill layers to be reinstated at a maximum depth of 150mm layers. The quantities are to be measured in final compacted layers only.

The unit of measure for sub-item (c) shall be the cubic volume of removed material measured in place prior to the removal thereof.

The rates are to include full compensation for all materials, labour, equipment and tools to work in restricted areas, transport and the making good of any damage to the oil dam during the reinstating of fill and removal of debris. The rates are to also include costs for spoiling the debris at registered dump sites should this be necessary.

## SANS 1200LB : BEDDING (PIPES)

#### VA-LB 3	MATERIALS

VA-LB 3.3	BEDDING

Add:

All bedding for rigid pipes shall be class B. Flexible pipes shall be bedded as shown on drawing LB 2 (a).

#### VA-LB 7	TESTING

VA-LB 7.1	DENSITY

The testing of backfill and bedding shall be as specified in SANS 1200 D Clause 7. Compaction is to be tested at the rate of at least one sand replacement field density test or two nuclear density tests for every 20 m³ of compacted backfill and bedding material. The provisions of SANS 1200 VA-D 7.2 shall apply to the use of a nuclear density meter.

#### VA-LB 8	MEASUREMENT AND PAYMENT VA-LB 8.1	PRINCIPLES

VA-LB 8.1.5	Disposal of Displaced Material

Delete and replace with

Displaced materials shall be carted to an approved spoil dump.

#### VA-LB 8.1.6	Free haul

Delete and replace with:

No overhaul will be paid. All haul will be freehaul.

## SANS 1200LE	: STORMWATER DRAINAGE

#### VA-LE 3	MATERIALS

VA-LE 3.1	CULVERT UNITS AND PIPES

  - Precast Concrete Pipes

Add:

Pipes shall be of the types and classes indicated on the drawings and shall have interlocking joints.

  - Skewed Ends

Whenever pipe culverts are cut on site the ends are to be repaired with a suitable wet to dry epoxy and cement mortar to restore cover to the reinforcing steel.

#### VA-LE 3.4	MANHOLES, CATCHPITS AND ACCESSORIES

VA-LE 3.4.1	Bricks

Amplify this clause as follows:

Bricks shall be NFX type with a nominal compressive strength of 10,5 MPa and shall comply with SANS 227.

#### VA-LE 3.5	GEOFABRIC BLANKET

Add new sub-clauses:

VA-LE 3.5.1	Geofabrics and the tests performed on them shall comply with SANS 0221. Tests shall be performed in an approved laboratory on samples of the materials and the following minimum values shall be

equalled or exceeded. Test results are to be submitted for every consignment.

VA-LE 3.5.2	Filter grade geofabric shall be a woven, non-woven or combination type of fabric. The permeability (SANS 0221 test method 3.7) shall be not less than 100 l/s per square metre. Penetration load (SANS 0221 test method 3.5) shall be at least 2,0 kN.

VA-LE 3.5.3	Strength grade geofabric shall be a woven type of fabric. The penetration load (SANS 0221 test method 3.5) shall be at least 4,5 kN. The permeability (SANS 0221 test method 3.7) shall be not less than 15 l/s per square metre.

#### VA-LE 5	CONSTRUCTION

VA-LE 5.1	TRENCH BOTTOM

VA-LE 5.1.2	Portal and rectangular culverts

Delete sub-clauses 5.1.2.1 to 5.1.2.3 and replace with:

The cast in situ invert slabs shall be constructed on 150 mm thick selected subgrade quality gravel compacted to 93% Mod. AASHTO density. Should the trench bottom be unsuitable for placing and compaction of the selected layer, the Supervisor may order the excavation to be taken out to a greater depth or may order the laying of a strength grade geofabric to strengthen the selected layer and separate it from the underlying soil.

#### VA-LE 5.2	BEDDING AND LAYING

VA-LE 5.2.2	Pipe Culverts

In sub-clause c) for 16 mm read 1,6 mm.

#### VA-LE 5.2.3	Concrete casing of pipelines

Amend as follows:

Concrete encasement and bedding shall be strength grade 20 MPa concrete. Add a new clause:

#### VA-LE 5.8	CULVERTS TO BE KEPT CLEAR

The Contractor is to regularly clear debris from the culverts during construction to ensure an open waterway. Before the work is handed over on completion, the culverts are to be cleaned and inspected by the Contractor.

#### VA-LE 8	MEASUREMENT AND PAYMENT VA-LE 8.2	SCHEDULED ITEMS

Add:

VA-LE 8.2.14	Supply and install sub-soil drains complete as indicated on drawing

D-FS-887 Sheet 02 detail 1	Unit: m

The unit of measure is the metre length of installed sub-soil drains as indicated on the drawings. The tendered rate shall include full compensation for all materials, equipment, labour and transport to construct the sub-soil drains as indicated on the dr

## C3.6 Particular Specifications

Particular specifications are given in the following sections.

- PB PARTICULAR SPECIFICATION: BUILDING WORK	50

- PZ PARTICULAR SPECIFICATION: OH&S SPECIFICATIONS AND STANDARDS	63

## PB	PARTICULAR SPECIFICATION: BUILDING WORK

### PB 1.	SCOPE

  - The specification covers the construction of buildings for control rooms, switchgear buildings, relay houses, transformer oil containment areas, “fire traps” and oil holding dams.

### PB 2.	GENERAL

  - This specification to be read in conjunction with Eskom’s Standard Specification and General Conditions of Contract.

  - The Contractor is to pay all fees with regard to services supplied by and for the Local Authority.

  - Portable latrines are to be provided and serviced by the Contractor

  - The Contractor is to include in his pricing for the temporary supply of water and power for construction purposes.

  - Reference specifications:

    - SANS 10400 – The Application of the National Building Regulations

    - National Building Regulations and Building Standards Act, 1977 (Act 103 of 1977)

    - Standard Drawing D-DT-5238 sheet 1 – 16 – NATIONAL STANDARD CONTROL    BUILDING DETAIL

PLAN, SECTIONS AND ELEVATIONS

    - Standard Drawing D-DT-5239 sheet 1 – 4 – NATIONAL STANDARD RELAY HOUSE PLAN, SECTIONS

AND ELEVATIONS

### PB 3.	FOUNDATIONS

  - Foundations General:

    - Standard soil classifications:

- “Type 1” soils: Competent soil with equal or better consistency (strength or toughness) than one would encounter in stiff cohesive soils or dense cohesionless soils above the water table. This soil must have a broad balanced texture (constituent particle sizes) with high average combinations of un-drained shear strength and internal angle of friction, with minimum values of 80kN/m² and 30° respectively. The minimum natural specific weight shall not be less than 18kN/m³. Maximum soil bearing pressure 300kPa.

- “Type 2” soils: A less competent soil than “Type 1", with equal or weaker consistency than one would encounter in firm to stiff swelling cohesive soils, or dry poorly graded loose to medium dense cohesionless soils above the water table. The minimum un-drained shear strength shall be 40kN/m², and the minimum natural specific weight shall not be less than 16kN/m³. Maximum soil bearing pressure 150kPa.

- “Type 3” soils: Dry loose cohesionless soil or very soft to soft cohesive soil. Maximum soil bearing pressure 100kPa.

- “Type 4” soils: Submerged cohesionless and cohesive soils. This includes all soils below the permanent water table, including soils below a re-occurring perched water table, or permeable soil in low-lying areas subjected to confirmed seasonal flooding. Maximum soil bearing pressure 50kPa.

- Summarized Geotechnical design parameters for various soil types:

| Design Parameter Unit | Soil Type |  |  |  |
| --- | --- | --- | --- | --- |
|  | Type 1 | Type 2 | Type 3 | Type 4 |
| Maximum Soil Bearing Pressure (kPa) | 300 | 150 | 100 | 50 |
| Maximum Toe Bearing Pressure (kPa) | 375 | 200 | 125 | 65 |
| Internal Angle Of Friction / Frustum Angle (degrees) | 30° | 20° | 0° | 0° |

    - For maximum soil bearing pressure and maximum toe bearing pressure, use the tabled pressure or 80% of the ultimate tested bearing pressure determined from appropriate tests.

  - Building foundations:

    - The depths and sizes of the foundations are to be as shown on the standard drawings D-DT-5238 and D- DT-5239.

| Soil Type | Dimensions (W x D) | Special Measures |
| --- | --- | --- |
| Type 1 | 700 x 250* | For compact non-cohesive soils consisting of gravels and sands located above the water table No reinforcing is required. |
| Type 2 | 700 x 250* | For stiffer or firm cohesive soils consisting of clays and silts, the foundation to have a single layer of Ref. 617 mesh reinforcing placed in the Centre of the foundation, i.e., 125mm from the bottom of foundation bottom. |
| Type 3 | To Be Designed | For soils consisting of soft clays and silts or submerged soils, the foundation is to be designed by a registered Professional Civil Engineer. |

* Walls of 220 mm and 280 mm without adjacent trenches are to have a 700 mm x 250 mm concrete foundation.

    - The concrete is to be class 15MPa concrete at 28days.

    - Reinforcing shall be as indicated on the detail drawings for each foundation type. For Type 3 foundations in soils containing soft clays, silts or submerged soils ( Type 4) the foundation and reinforcement shall be design and by a registered Professional Civil Engineer Technologist.

### PB 4.	WALLS

  - Building Walls:

    - For sections of the wall below ground, well burnt red hard clay R.O.K Bricks.

    - For internal walls: Red Clay R.O.K. Bricks are to be used (min. compressive strength: 7MPa)

    - For face bricks: Clay face bricks. Smooth or Rustic Iron spots, min. 35MPa) or as approved by Eskom. The use of face bricks is to start 1 course below the final ground line.

    - Cavity walls to be 110 – 60 110 skins with 60mm cavity.

    - Brick force: 75mm wide or 150mm wide galvanized brick force to be applied to the first four courses above the foundation and on the top 4 courses below the wall plate.

    - Gables are to be applied at every 4th course to the ridge.

    - Wall ties: Galvanized Butterfly type, 5/m² in the wall at 300 mm c/c at jambs.

    - Damp Proof Course: Gunplas Brikgrip 375 microns, stepped at floor level in cavity walls and around openings.

    - Joints: Face brick, 10 mm raked, all other joints to be keyed for plastering. Every 4th joint to be perpendicularly above stepped damp proof course to be raked clear to drain the cavity.

    - Mortar is to be mixed at a ratio of 1:4 (cement: sand).

    - Top 3 courses of cavity below truss to be filled with concrete.

    - For “Combo” Control Room 340mm x 340mm face brick piers to be reinforced with 2 x Y12 bars. Cavity to be filled with concrete. Piers required to buttress external walls at 5000mmm centers.

### PB 5.	PLASTERWORK

  - Internal plasterwork is to be 15 mm thick and smooth steel float finished. The plaster is to be mixed to a ratio of 1:1:6 (cement: lime: sand).

  - External plasterwork to be 20mm thick, wood floated. The plaster is to be mixed to a ratio of 1:4 (cement: sand).

### PB 6.	FLOORS & FLOOR FINISHES

  - Eskom Accepted cementitious dry shake surface floor hardener to be applied to the manufacturer’s specification on 100 mm thick, 30MPa strength concrete. The service bed is to be constructed on the compacted sand fill, constructed in 150mm thick backfill layers.

  - The floor to be steel power floated to a hard level surface.

  - All floors are to be reinforced with REF 395 or 617 weld mesh. Minimum cover of 50mm from the bottom of slab. Refer to specified detailed drawing. Reinforcing to be carried though into the platforms.

  - Floor level to be laid to a tolerance of 0.5 m per meter with a maximum of 2.5mm difference over the entire length.

  - Steps and loading bay to have a 150m brush finish, 30MPa concrete cast to a slope as shown on the drawings. Reinforcing to be the same as for the Switch room floor.

  - Relay and Switch Room to have 2 coats of an Eskom accepted transparent floor sealer or equal approved equivalent. Product to be applied after the commissioning of electrical equipment.

  - For the Relay room and W/C: a natural grey finish is to be applied.

  - The Battery room is to have a sloping floor of 25mm to a glazed floor channel. Alternatively, the Battery room floor would be ceramic nonslip acid resisting tiles fixed with acid resistant tile adhesive and grouting.

### PB 7.	ROOF & CEILING

  - For Relay House:

    - Big Six or Profile B 6mm fiber cement or 0.6 mm galvanized IBR sheeting on 76 mm x 50 mm purlins at maximum 1400 mm c/c or 1050 mm c/c on gangnail type trusses.

    - Where gang nail trusses are not available the Contractor shall use 150 mm x 38 mm rafters and tiebeams and 114 mm x 38 mm struts. All joints to be galvanized and bolted with M12 bolts.

    - 114 mm x 38 mm wall plates to be tied 600 mm into the brick wall. With galvanized hoop iron straps.

    - Contractor to obtain a certificate of compliance from the Roof Truss manufacturer.

    - 4mm Nutec fibre/cement ceiling on 50 mm x 38 mm brandering at 400 mm c/c. Joints are to be taped for painting.

    - 75mm thick Aerolite or approved equivalent roof insulation to be applied over the ceiling.

  - For “Combo” Control Building:

    - “Megaspan” or approved equivalent 0.6mm galvanized IBR Sheeting in 4200mm lengths bonded to 4mm Sagex core with either 0.4mm Chromadek ceiling or 4mm Nutec fibre/cement ceiling.

    - Supports to be 220mm x 69mm PAR SA Pine beams as shown. Beams to be spaced at , maximum, 1735mm c/cs.

    - Truss construction for Relay/Switch room more than 6000m in length supporting truss to be constructed at mid span or every 5000mm. refer to drawing D-DT-5238 Sheet 15 Rev 01 for more details.

    - Truss to be tied to the brickwork with galvanized hoop iron straps (wallplates) embedded 600m deep into the brickwork.

    - Contractor to obtain a certificate of compliance from the Roof Truss manufacturer.

### PB 8.	ROOF DRAINAGE & WATERPROOFING

  - Roof Drainage shall be done by 140mm high x 130mm wide standard galvanized steel gutters. The gutters shall be fixed to roof sheeting at 515mm centres with standard galvanized steel or standard equivalent aluminium brackets.

  - All bends and downspout fittings of standard galvanized steel shall also be supplied and installed.

  - The Contractor shall install standard galvanized steel down pipes and gutter outlets over 1000mm x 150mm precast concrete rainwater channel outlets. The down pipes shall be supported bu standard galvanized steel brackets at the supplier specified bracket spacing, capable of supporting the down pipes.

### PB 9.	DOORS

9.1. Doors are to be of the type specified and installed according to the details on drawing D-DT-5239 sheet 04, latest revision for the Relay house. Drawing D-DT-5238 sheet 16, latest revision for the “Combo” Control building.

### PB 10.	WINDOWS

10.1.  Windows are to be Wespeco® type NCF5 galvanized steel or approved equivalent. The glazing is to be 6mm Georgian wired cast.

### PB 11.	AIR FILTERS & FRAMES

  - The number of air filters is to be determined by the length of the building.

  - WinBlok® WB66, 600mm x 600mm x 300mm deep. Rebate to Winblok® tp be on external skin of wall, facing outwards.

  - Winlouvre® WL (A)66 fitted with nat anodized aluminium louveres externally.

  - Burglar bars to be 20m x 6mm galvanized steel with Ø:8mm galvanized twist off nut expansion bolts. Burglar bars to be supplied by WinBlok® and to be installed/fixed on site by the Contractor.

  - Air filter frames to be 55mm x 40mm x 1.6mm formed galvanized mild steel channels. Outer holes to flange to be Ø: 20mm, with Ø:7mm holes to the inner flange (against wall) for 30mm long x Ø:6mm CSK fixing screws.

  - Air filter frame to fit “Fibratron” WP77 594mm x 594mm x 48mmm washable filters or equivalent approved products.

### PB 12.	SERVICE TRENCHES

  - Service trench walls to be bagged brick, all trench covers and channels to be constructed by the Contractor. Refer to drawing D-DT-5238 sheet 13, latest revision for details.

  - Service trench covers to be 4.5mm steel “vastrap” chequer plate with Ø: 25mm lifting holes.

### PB 13.	SWITCHGEAR RACK OUT STEEL PLATES:

13.1. Contractor to fix in position (after installation of switchgear by specialist Contractor) 3mm thick x 1225mm galvanized steel plates with CSK stainless steel screws at 2500mm centres. The Contractor is to refer to the design document as to the extent (lengths) of the plates required.

### PB 14.	SANITARY WARE

  - The battery room sink is to be in accordance with drawing D-DT-5238 sheet 14.

  - The W/C is to be Vaal Klip suite white vitreous china with seat and lid.

  - Cobra Star stop valve and toilet roll holder.

  - The basin is to be Vaal Bantam 455 mm x 290 mm white vitreous china complete with wall brackets, plug & chain and cobra star cold water tap only.

  - Hose tap is to be Cobra N108LK.

### PB 15.	PAINT

  - Galvanized steel is to have galvkleen applied followed by 1 coat calcium universal undercoat, I coat of gloss enamel, colour brilliant white.

  - Internal walls & ceilings are to have 1 filler coat and 2 coats of an Eskom accepted durable PVA. The colour is to be white. The final coat of paint will only be applied after the final commissioning of all electrical equipment by Eskom.

  - Battery room walls and ceiling will have 3 coats super silk acrylic acid resisting paint. The Battery room floor will have 2 coats of Epoxy acid resisting floor paint. The colour of the floor paint is to be grey. Floor primer be a Sikaguard 62 with Sika 73 primer shall be applied to the manufacturer’s specification or Eskom approved equivalent.

  - Trusses, purlins, wall plates and rafter ends, backing piece and exposed trusses are to have one coat pink primer and 2 coats of flat enamel applied.

  - Steel work: Galvanized steel is to have galvkleen applied followed by 1 coat calcium universal undercoat, 1 coat of gloss enamel, colour brilliant white.

  - Trench covers: 1 coat red lead primer, 1 coat undercoat, 2 coats eggshell enamel. Colour: light grey to Eskom approval.

### PB 16.	WATER SUPPLY

16.1. Water supply is to be supplied by 15mm or 20mmm copper pipes from the water supply tank to the W/C, external tap, basin and battery sink. Refer to the detailed drawings for the correct water supply pipe diameter.

### PB 17.	AIR BRICKS

17.1. External air bricks are to be 220 mm x 150 mm cement face and internal air bricks are to be 220 mm x 150 mm plastic face with vermin proofing. Both are to be set flush into the wall. Two will be required in accordance with drawing D-DT-5239. They are to be mounted 150 mm above the final floor level in the positions shown.

### PB 18.	CONVECTIONAL AIR VENT

18.1. “Whirlybird” air ventilation system, or approved equivalent, to be installed in accordance with the manufacturers’ specifications. Ø 300mm. The number of vents to be specified.

### PB 19.	HANDRAILS

  - Inter-link handrail system to be supplied and installed as indicated on the detail drawings.

  - All “Wecrolok ®, or approved equivalent, handrail systems are to be installed as per the manufacturer’s specifications. handrail

### PB 20.	CABLE RACKS

  - Cable racks shall be supplied and installed by the Contractor.

  - Cable racks shall be 600mm wide wire mesh type trays, 2800mm above the final floor level, robustly supported and fixed to the walls in order withstand the loads of the cables which shall be installed in the building.

### PB 21.	POWER & LIGHTING

  - All Electrical work shall be carried out in strict accordance with the latest revision and requirement of the SANS 10142-2017: The Wiring of Premises.

  - AC/DC Board supplied and installed by Eskom. The Electrical Contractor to supply and hang all light fittings. All wiring to these fittings shall run surface and terminate in a Sub Board as shown on the plan. If no position is indicated on the plan, the Clerk of Works and Engineer will provide a position on site.

  - The Contractor shall wire conduit and terminate wiring at the Sub Board supply cable above the AC/DC Board. Top of the Eskom AC/DC Board is as shown on the AC/DC board drawings.

  - Wiring shall be P.V.C sheathed in white plastic conduit (with SANS mark). All conduit to be run surface in straight lines.

  - Switches shall be SANS approved surface mounted toggle type mounted in the Sub Board. For relay rooms they shall be surface mounted toggle type, mounted 1200mm above the final floor level. External sockets shall be weatherproof cam type to Eskom approval

  - All lighting fittings are to have SANS mark. Fittings shall be fixed to the flat ceiling and 3400mm above final floor level. Light fittings for the Battery Room shall be mounted against the wall at 2800mm above the final floor level.

  - Battery Room extractor to be LUFT or approved equivalent, 12 BWX/4D/EXE 3 phase flameproof motor with standard PVC coated heavy gauge wire guards fitted to inside and standard glass fiber wall cowl fitted to outside. The unit shall be switched from the AC/DC board. The fan shall have a 3-pole isolator mounted at high level externally next to Battery room door.

  - Ceiling Fans, where required, shall be 1400mm dia aluminium blade single phase with 5 speed wall mounted choke type regulator. The fans shall have 315mm anti-vibration mounting and ceiling hook as Donkin Summering “Coolflo” or approved equivalent. The maximum distance between fans shall be 500mm. For mounting below sloping ceilings the mounting point shall be suspended from the 144mm x 69mm timber beam, fixed to the roof beams/purlins.

  - Time switch for AC Light switches shall be Coupaton C53-T125, 240V / 16A, 60 minute or approved equivalent.

  - Contactor for AC Lights shall be Lovato BF12 with 220V coil or approved equivalent.

  - Timer Box shall be surface mounted Gewiss GW 44207 or approved equivalent.

  - Emergency Lighting shall be provided in the buildings. For emergency lighting one tube in the fitting shall have an additional conduit run from the DC side of the distribution board which will include 1 x positive, 1 x switched positive and 1 x negative wire.

  - The Contractor to supply and install a 220V DC to 220V AC inverter in the fitting and a contactor rated at 10A in the Sub Board for the emergency lighting fitting. Affected fittings and end caps to be painted red in order to differentiate between fittings. The Contractor shall supply and fit the required switch and timer on wall as indicated on the drawings. The Wiring shall be connected by authorised Eskom personnel to the AC/DC Board.

  - Inverters to affected emergency lighting to be fixed into the fittings and replace he normal ballast. The inverter to be 220V, DC input and 1 x 60W output. The inverter shall be as supplied by Smith Walker inverters or approved equivalent.

  - Luminance levels for Switch/Relay and Battery Room is 300 Lux, Storeroom and WC is 160 Lux.

  - Emergency lighting shall require 1 tube for every 60 m² of room area.

  - Main circuit breakers are to be rated at 5kA.

  - Earth Leakage unit shall be HY-MAG or approved equivalent.

  - Socket Outlets shall be 15A 3 pin round, surface mounted. 3 socket outlets are required.

  - The Sub Board/ Distribution board shall be supplied and installed and wired by the Contractor. The Sub Board shall be clearly labelled and marked in strict accordance with the requirements of SANS 10142. The Sub Board shall be surface mounted and shall be large enough to accommodate the following:

    - 1 x 3 Pole Isolator,

    - 1 x Earth Leakage Unit,

    - 1 x MCB for the Lights circuit,

    - 2 x MCB’s for Socket Outlet circuits,

    - 1 x Day/Night Switch for the yard lights,

    - 1 x Contactor rated for the yard lights,

    - 1 x MCB for the “Day/Night Switch Bypass circuit,

    - 1 x MCB for the Ceiling and Ventilation Fan circuit.

  - All details regarding type and rating of all fittings are indicated on the detail drawings.

  - The Contractor shall submit a Certificate of Compliance for all Electrical installations performed by themselves or their delegated sub-Contractors. This Certificate of Compliance is to be prepared and submitted in strict accordance with the SANS 10142: Wiring of Premises. The Certificate of Compliance is also to be issued by Organisations of Persons which have been registered in good standing with the Electrical Contractors Association.

### PB 22.	MEASUREMENT AND PAYMENT

  - Scheduled items:

    - Construction of control building complete as indicated	Unit: m²

on drawing D-DT-5239, ….m long.

The unit of measurement will be the square meter area of the variable length control room building, complete as indicate in the standard drawings. The final length of the building is to be indicated.

The rate is to include the cost of procurement of all the required materials, transport, labour, equipment and finishing, complete as indicated on the standard drawings.

### Construction of switchgear building complete as indicated	Unit: m²

on drawing D-DT-5238, ….m long.

The unit of measurement will be the square meter area of the variable length switchgear building, complete as indicate in the standard drawings. The final length of the building is to be indicated.

The rate is to include the cost of procurement of all the required materials, transport, labour, equipment and finishing, complete as indicated on the standard drawings.

### Control / Relay Room Cable Racks – Ladder Type

      - Mounting Plates / Brackets	Unit: no

Separate items shall be scheduled for the various mounting plates as per the detailed drawings.

      - Cable Racks	Unit: no

Separate items shall be scheduled for the various lengths of cable racks as per the detailed drawings.

      - Erection Bolts	Unit: no

Separate items shall be scheduled for the various bolt types, sizes and lengths as per the detailed drawings.

      - Earthing of Cable Rack	Unit: no

Separate items shall be scheduled for the earthing of the cable racks as per the detailed drawings.

The unit of measurement shall be the number (no) of items to be supplied and installed as per the detailed drawings.

The rate shall include full compensation for all materials, labour, transport, equipment and plant required to supply and install the scheduled items.

### Control / Relay Room Building Refurbishment or Extension:

      - Masonry	Unit: m³

Separate items as scheduled

      - Paint Application to walls and ceilings	Unit: m³

Separate items as scheduled

      - Floors	Unit: m²

Separate items as scheduled

The unit of measurement will be as scheduled above. Reference is to be made to the standard substation Control Room / Relay Room drawings and the project specific control room drawings applicable to this project.

The rate shall include all costs for the procurement of all materials, all transport, labour and equipment to complete each scheduled item.

      - Roof

        - Roof Trusses and Battens	Unit: Sum

The unit of measure shall be the sum cost to design, supply and erect the roof trusses and battens as per the manufacturer/supplier’s requirements and in accordance with SANS 10400: Building Regulations.

The tendered rate shall include full compensation for all consultations and site visits by the professional design team, all labour, all materials, all transport and all plant and equipment required to erect and install the roof structure in accordance with the Manufacturers’ requirements and the SANS 10400.

        - Roof Sheeting	Unit: m²

The unit of measure shall be the square meter area (m²) of roof sheeting to be supplied and installed in accordance with SANS 10400: Building Regulations.

The tendered rate shall include full compensation, all labour, all materials, all transport and all plant and equipment required to supply and install the roof sheeting in accordance with the Manufacturers’ requirements and the SANS 10400.

        - Brandering, Ceiling and Roof Insulation	Unit: m²

The unit of measure shall be the square meter area (m²) for the scheduled items.

The tendered rate shall include full compensation, all labour, all materials, all transport and all plant and equipment required to supply and install the scheduled items in accordance with the Manufacturers’ requirements and the SANS 10400.

        - Roof Gutters

          - Remove and replacement of existing Control / Relay Room roof

gutters and down pipes	Unit: m

The unit of measure shall be the meter (m) length of gutters to be removed and replaced as per the detailed drawings.

          - Supply and install Ø: precast concrete rainwater channel -1.0m long	Unit: no

The unit of measure shall be the number (no) precast concrete rainwater channels supplied and installed as per the detailed drawings.

The tendered rate shall include full compensation, all labour, all materials, all transport and all plant and equipment required to supply and install the scheduled items in accordance with the detailed drawings and the SANS 10400.

      - Structural I-Beam for Cable Rack Support

        - Supply and installation of I-Beam, XXX x XXX x XXX of nominal length of XXm	Unit: no

The unit of measure shall be the number (no) structural I-Beams supplied and installed as per the project drawings.

The tendered rate shall include full compensation for, all labour, all materials, all transport and all plant and equipment required to supply, deliver, and install the scheduled structural element in accordance with the detailed drawings

      - Installation of temporary building support props	Unit: no

The unit of measure shall be the number (no) of temporary building support props to be installed to support the building during the installation of other permanent works.

The tendered rate shall include full compensation for, all labour, all materials, all transport and all plant and equipment required to supply, deliver, and install the temporary building support props.

      - Manufacture, supply, and installation of additional cable trench support	Unit: no

base frames as per Drawings CORP 2826 A002. Supplied complete with mounting bolts and additional checker plate covers.

The unit of measure shall be the number (no) of base support frames manufactured, supplied, and installed.

The tendered rate shall include full compensation for, all labour, all materials, all transport and all plant and equipment required to supply, deliver, and install the additional support base frames.

### Power and Lighting:

      - Light fittings and Switches	Unit: no

Separate items as scheduled

The unit of measurement shall be the number of scheduled light fittings and switches as indicated in the detailed drawings and detailed specifications.

The rate is to include the cost of procurement of the materials, transport, labour, equipment , wiring, blanking plates, wall boxes, covers, conduit, saddles, inspections boxes, joints and any other item deemed necessary to complete the installation in accordance with SANS 10142-1 complete as indicated on the standard drawings.

      - Socket Outlets	Unit: no

Separate items as scheduled

The unit of measurement shall be the number of scheduled socketed outlets as indicated in the detailed drawings and detailed specifications.

The rate is to include the cost of procurement of the materials, transport, labour, equipment, wiring, blanking plates, wall boxes, covers, conduit, saddles, inspections boxes, joints and any other item deemed necessary to complete the installation in accordance with SANS 10142-1 complete as indicated on the standard drawings.

      - Surface-mounted timer box	Unit: no

The unit of measurement shall be the number of surface-mounted timer boxes as indicated in the detailed drawings and detailed specifications.

The rate is to include the cost of procurement of the materials, transport, labour, equipment, wiring, blanking plates, wall boxes, covers, conduit, saddles, inspections boxes, joints and any other item deemed necessary to complete the installation in accordance with SANS 10142-1 complete as indicated on the standard drawings.

      - Surface-mount Sub Board / Distribution Board	Unit: no

Separate items as scheduled

The unit of measurement shall be the number of scheduled items required for the complete installation of a surface-mount sub board / distribution board and all the related circuit breakers, isolators, etc. as indicated in the detailed drawings and detailed specifications.

The rate is to include the cost of procurement of the materials, transport, labour, equipment , wiring, blanking plates, wall boxes, covers, conduit, saddles, inspections boxes, joints and any other item deemed necessary to complete the installation in accordance with SANS 10142-1 complete as indicated on the standard drawings.

      - Issuing of an Electrical Certificate of Compliance	Unit: sum

The unit of measurement will be the sum for the issuing of an electrical certificate of compliance of the electrical installation in accordance with the SANS 10142-1 by an Authorised Person.

The rate is to include the cost of transport, labour, equipment and any materials required to issue the certificate and completion of any work not deemed to be incompliance with the SANS 10142-1.

### Repair of existing Control Room and Relay Room:

      - Water proofing and sealing of roof	Unit: m²

      - Clean, prime and paint roof	Unit: m²

      - Repair of existing Control Room / Relay Room Door	Unit: no

      - Replacement of Control Room / Relay Room Door	Unit: no

      - Remove and replacement of existing Control Room /	Unit: m

Relay Room Door roof gutters

      - Control / Relay Room Roof

        - Roof Trusses and battens	Unit: sum

Separate items as scheduled

        - Roof Sheeting	Unit: no

Separate items as scheduled

        - Brandering, Ceiling and Roof Insulation	Unit: m²

Separate items as scheduled

      - Control / Relay Room Wall and Wall Finishes	Unit: m²

Separate items as scheduled

      - Control / Relay Room Floor and Floor Finishes	Unit: m²

Separate items as scheduled

      - Crack repair on existing walls and plaster	Unit m²

The unit of measurement shall be the square meter area (m²) of treated and repaired cracks to plaster and walls.

The unit of measurement will be as scheduled above. Reference is to be made to the standard substation Control Room / Relay Room drawings for details.

The rate shall include all costs for the procurement of the materials, all transport, labour and equipment to complete each scheduled item.

## PZ	PARTICULAR SPECIFICATION: OH&S SPECIFICATIONS AND STANDARDS

### PZ 1	Constraints on how the Contractor Provides the Works

  - Constraints on how the Contractor Provides the Works

### Quality Plan

      - The Contractor shall submit a quality plan indicating the control points for quality to ensure that the works are done according to specification.

      - The Contractor shall employ a competent Supervisor or Foreman on site for the duration of the project to implement workmanship quality checks.

      - Eskom shall do inspections and quality checks on installations completed by the Contractor prior to hand- over of each project.

### Access to the site

      - The Employer shall provide the Contractor with an Access Certificate to formally provide access to the site and works implementation. Copy of the signed Access Certificate is to be kept on site for the duration of the project.

### Interaction with Customers / Parties affected

      - The Contractor shall be responsible for negotiation with customers with regard to use of access routes on farms etc.

      - The Contractor shall be responsible for negotiation with land or business owners and / or the Local Authority with regard to the works.

      - The Contractor will be responsible for external disputes which may occur with regard to the works.

      - The Contractor is required to make all the necessary arrangements with the Local Authorities for road crossing structures and removal thereof, eg. Removal of pavements, thrust boring under roads, way leaves, etc.

### Carrying out the works

      - The Scope of “Works” is an extension of the drawings, specifications and bills of quantities listed.

      - The Contractor shall notify the Employer of any discrepancies before commencement of the works

      - The onus is on the Contractor to obtain the latest revision of standards applicable.

      - The Contractor is required to supply all material, labour, plant, equipment, loose tools, consumables and transport for the duration and completion of the project unless alternatively requested in the “Services Supplied - Section 5”.

      - Contractor to provide summary of all costs for the execution of the works of the complete project.

      - The Contractor must immediately notify the Employer in writing of scope and site variations.

      - The Contractor will report all obstacles on site that could impact negatively on time and cost in writing to the Employer

      - Contractor to clear and de-establish total site on completion of proposed works.

      - Contractor is required to clear and cart away rubble and surplus works

    - Clerk of Works (COW)

      - Clerk of Works has been appointed and will inspect Safety, Quality and Quantities. The COW is the Eskom Representative on site and his instructions must be followed. A COW inspection form will be completed on site. Should the team fail to comply with all the requirements, Clerks of Works have all the rights to instruct that particular team to immediately vacate the site premises

### Performance Management

      - The Contractor’s Performance will be assessed in accordance with Eskom Performance Appraisal Process.

### Health and Safety Management

      - The Contractor shall comply with:

        - The Occupational Health and Safety Act, 1993, and all regulations made there under as per the standard clause A1, stipulated on page 4 of this contract.

        - The Construction Regulations, 2003.

        - The Health and Safety Requirements of the Employer more fully set out in Distribution Standards DISPVABF3 (The Contractor will sign the attached pages of the specification as acknowledgement of receipt and adherence) and SCSPVABN2.

        - All Eskom Safety and Operating Procedures as outlined in the ORHVS (Operating Regulations on High Voltage Systems) and the standards attached to this document.

        - The Contractor acknowledges that he is fully aware of the requirements of all of the above and undertakes to employ people who have been duly authorized in terms thereof and who have received sufficient safety training to ensure that they can comply therewith.

      - The Contractor undertakes not to do, or not to allow anything to be done which will contravene any of the provisions of the Act, Regulations or Safety and Operating Procedures

      - The Contractor shall ensure that a team member of the Contractor is authorized as a Responsible Person in terms of the ORHVS. This includes the completion of all the pre-authorization training required for ORHVS Responsible Person (at the Contractor’s expense) as detailed in SCSPVBN2. The Responsible Person shall supervise the works at all times and be available to take permits where necessary.

      - The Contractor shall ensure that the Responsible person completes a training logbook (as per SCSPVBN2) and arrange with the appropriate Eskom Representative for evaluation of the authorized person prior to the Construction start date. This needs to be arranged by the Contractor.

      - The Contractor shall appoint a person who will liaise with the Eskom Safety Officer responsible for the premises relevant to this contract. The person so appointed shall:

        - Supply the Eskom Safety Officer with copies of minutes of all Health and Safety Committee meetings (if relevant), on a monthly basis.

        - Supply the Eskom Safety Officer with copies of all appointments in respect of employees employed on this contract, in terms of the Act and Regulations and shall advise the Eskom Safety Officer of any changes thereto – to be handed over to the Employer prior to construction start.

      - Eskom may, at any stage during the currency of this agreement, be entitled to.

        - Do safety audits at the Contractor’s premises, its workplaces and on its employees.

        - Reefs to employee, sub-Contractor or agent of the Contractor access to its premises if such person has been found to commit any unlawful act or any unsafe working practice or is found to be not authorized or qualified in terms of the Act

        - Issue the Contractor with a work stop order or a compliance order should Eskom become aware of any unsafe working procedures or conditions or any non-compliance with the Act, Regulations and Procedures referred to in 1 above by the Contractor or any of its employees, sub-Contractors or agents.

      - No extension of time will be allowed as a result of any action taken by Eskom in terms of the above and the Contractor shall have no claim against Eskom as a result thereof. Furthermore, no amendments to the Act or the Regulations or reasonable amendment to Eskom’s Safety and Operating Procedures will entitle the Contractor to claim any additional costs incurred in complying therewith from Eskom.

      - An authorized Eskom Representative will be on site for regular site visits to monitor the Contractor’s implementation of health, safety and quality Standards.

      - The works to be enclosed with chevron barricade tape supplied and installed by the Contractor and set out by the Employer.

      - The Contractor shall be responsible for all expenses incurred to ensure adherence to Health and Safety Regulations as stipulated above which includes but is not restricted to ORHVS training courses, etc.

      - The Contractor shall adhere to the Standard on Working Clearances at MV Structures with pole-mounted auxiliary equipment as attached to this contract.

      - The Contractor shall comply with all the requirements of the CONSTRUCTION REGULATIONS.

      - Please Note: (Before carrying out work, Contractor to notify the provincial director in writing of the construction work if it is exceeding the limits as listed in the Construction Regulations)

      - It is an Eskom requirement that the Contractor shall use a Fall Arrest System (FAS) as defined in the Construction Regulations whenever a risk of falling exists. The Contractor shall adhere to the applicable standards and procedures attached to this contract.

Typically, the following identified risks could endanger the work constructed by the Contractor. The Contractor

should identify mitigation actions for these risks, as well as identify any additional risks and notify the Employer.

| Typical Risk | Yes/No |
| --- | --- |
| Live underground cables | Yes |
| Work in live chambers/restricted areas | Yes |
| Live overhead conductors/crossings | No |
| Close proximity work to live equipment | No |
| Work in elevated positions/on ladders/from crane buckets | No |
| Operating of cranes/vehicle mounted | No |
| Static electricity/induction, step potential etc | Yes |
| Work with chainsaws/mechanical cutters | No |
| Materials handling/ heavy equipment handling | Yes |
| Conductor stringing and tensioning | No |
| Vehicle risks | Yes |
| Work in open trenches/excavations | Yes |
| Biological/Health risks (camps) | No |
| Weather related risks (UV, heat, cold) | Yes |
| Environmental risks | No |
| Ergonomic risks (body position, fatigue) | Yes |
| Work on/dismantling of rusted & rotten poles and structures | No |
| Fire risks | No |

| Typical Risk | Yes/No |
| --- | --- |
| Public safety risks | No |

### Construction Safety

      - The Contractor shall be responsible for ensuring that all equipment supplied and used and all work carried out under this contract shall be in accordance with the Occupational Health and Safety Act (Act 85 of 1993) and regulations remaining in force, as may be amended from time to time.

      - In addition, the Contractor shall comply with other Safety application provisions of Government, Provincial, Municipal Safety Laws, Building, Construction, Electricity Regulations and Eskom Distribution Standards.

      - The Contractor shall accept full responsibility for the means, methods, sequence or procedures of construction for safety precautions or programmers incident to the work of the Contractor.

      - The Contractor is required to submit a working methodology statement with regards to the Safety Standards while working within hazardous areas such as live substations or in close proximity of energized apparatus.

      - The Contractor shall indemnify the Employer and the Engineer against responsibility for safety on the site of the works.

      - The Contractor shall enter into an agreement to complete the work required for the construction of the works in accordance with the provisions of all pertinent legislation and in particular with the provisions of the Occupational Health and Safety Act (Act 85 of 1993) and the regulations promulgated there under.

      - Reference of the Safety Methodology Statement can be found in the Government Occupational Health and Safety Act (Act 8 of 1993) and Construction Regulations Document which is available publicly.

      - The safety of the Contractors personnel and employees acquire precedence over the construction works.

      - Contractor to assess and make provision for security services to protect the demolished material should the need arise

### Compensation for Occupational Injury and Diseases Act

      - The Contractor shall submit with his tender proof of adherence to the above act.

      - General Environmental Management Requirements

      - The Contractor shall receive an Environmental Management Plan –EMP (normally as part of the DESD) and must adhere to all its requirements.

      - Contractor to provide toilet facilities, water and electricity.

      - All environmental legal Liabilities and claims arising from the negligent activities of the Contractor shall be for the Contractors expense.

      - The Contractor shall have an understanding of Eskom’s basic environmental principles and commitments (covered during Eskom Environmental Law Course)

# Drawings

| Detail Drawings |  |  |
| --- | --- | --- |
| Drawing no | Sheet | Title |
| D-FS-887 | 1 | DETAIL 1, 3, 5 – CABLE TRENCHES |
| D-DT-5237 | 1-9 | FENCING |
| 0.54/8282 | - | NON-LETHAL ELECTRIFIED FENCING |
| D-DT-5238 | 1 – 16 | BUILDINGS |
| D-DT-5239 | 1 – 4 | BUILDINGS |
| D-DT-5240 | 1 – 21 | EARTHING |
| D-DT-5231 / 5232 / 5233 / 5236 | 1 – 2 | TRANSFORMER PLINTHS AND RELATED |
| D-DT-5234 | 1 – 9 | OIL DAMS |
| D-DT-5233/41 | 1 – 2 | OIL CONTAINMENT - OIL DAM |
| D-DT-5252 /5257/5260/5265 | - | COLUMNS AND BEAMS |
| D-DT-5245 / 5247 | - | CIVILS: KERBING, TRENCHING, LV CABLE CROSSING, GATE RAMPS |
| D-DT-5273 / 5274 | 1 – 4 | LABELS AND SIGNS |
| D-DT-5275 | - | FIREWALL (BRICK) |
| Project Specific Drawings |  |  |
| Drawing no | Sheet | Title |
| D-FS-18176 | 1-2 | SASOL CHEM 88/11kV SS BREAKER ROOM FLOOR AND CABLE TRENCH MODIFICATION |

- Specifications

| Title | Date or revision | Tick if publicly available |
| --- | --- | --- |
| OCCUPATIONAL HEALTH AND SAFETY STANDARD FOR CONTRACTORS AND SUBCONTRACTORS WORKING FOR ESKOM | DISPVABF3 |  |
| PROCEDURE FOR REFUSAL TO WORK ON GROUNDS OF HEALTH AND SAFETY | SCSPVABP6 REV 0 |  |
| CONTRACTOR HEALTH AND SAFETY PLAN – TO BE COMPLETED AND SUBMITTED AT TENDER STAGE |  |  |
| CONSTRUCTION, SAFETY, HEALTH AND ENVIRONMENT MANAGEMENT IN ESKOM | EPC 32-136 REV0 |  |
| ACKNOWLEDGEMENT OF OCCUPATIONAL HEALTH AND SAFETY STANDARD FOR CONTRACTORS AND SUBCONTRACTORS WORKING FOR ESKOM |  |  |
| GOVERNMENT OCCUPATIONAL HEALTH AND SAFETY ACT – CONSTRUCTION REGULATIONS | PUBLICLY AVAILABLE |  |
| TRAINING, TESTING AND AUTHORIZATION OF PERSONS FOR THE OPERATION AND MAINTENANCE OF THE POWER SYSTEM | SCSPVABN2 |  |
| THE TRAINING LOGBOOKS FOR AUTHORIZATION OF PERSONS FOR HIGH-VOLTAGE | SCSAMAAE5 REV 1 |  |
| PROCEDURE TO FOLLOW WHEN THE INTEGRITY OF EARTH CONTINUITY CONDUCTORS CONNECTING APPARATUS TO THE EARTHMAT IS SUSPECT | SCSPVABFO REV 0 |  |
| IDENTIFYING, ANALYSING, DOCUMENTING AND OBSERVING DANGEROUS / HAZARDOUS TASKS | SCSPVACKO REV 0 |  |
| REPORTING, RECORDING AND INVESTIGATION OF INCIDENTS | ESKPVABN9 REV 1 |  |

| Title | Date or revision | Tick if publicly available |
| --- | --- | --- |
| PROCEDURE FOR BARRICADING | SCSPVABF4 REV 0 |  |
| STANDARD FOR THE CONTROL AND APPLICATIONS OF MASTER LOCKS AND ISSUE OF MASTER KEYS | SCSASAAU1 REV 0 |  |
| ROUTINE INSPECTIONS OF ELECTRICAL EQUIPMENT | SCSASABA8 REV 0 |  |
| CLEARING AND MAINTENANCE OF SERVITUDE ROUTESSCSASAAZ9 REV 0TRAINING, TESTING AND AUTHORIZATION OF PERSONS FOR THE OPERATION AND MAINTENANCE OF THE POWER SYSTEM | SCSPVABN2 REV 0 |  |
| STANDARD APPLICABLE TO CONTRACTORS WORKING IN CLOSE PROXIMITY TO LIVE APPARATUS | SCSASAAW8 REV 1 |  |
| PROCEDURE FOR THE IDENTIFICATION OF RISK PRIOR TO THE COMMENCEMENT OF WORK | SCSPVABB2 REV 1 |  |
| STANDARD FOR THE USE OF EQUIPOTENTIAL EARTH FOOTPLATES | SCSASAAU5 REV 0 |  |
| MV AND LV POLE IDENTIFICATION | SCSASABZ5 |  |
| ACCESS TO FARMS | DGL_34-190 |  |
| BUSINESS CONDUCT POLICY AND GUIDELINES | ESKPBAAN4 REV1 |  |
| LOCAL STANDARD FOR THE OPERATING OF HIGH CUTTER / CHAIN SAW | NETOM7 REV 0 |  |
| RELEVANT STANDARDS AS LISTED IN THE DOCUMENT CALLED THE DESIGN DOCUMENT |  |  |
| PROCEDURE FOR THE REPORTING, INVESTIGATION, COSTING AND FOLLOW UP ON INCIDENCES \ACCIDENTS | DPC -34-350 |  |
| ENVIRONMENTAL LIAISON COMMITTEE (ELC) PERFORMANCE INDICATOR REPORTING PROCESS | EPC -32 -249 |  |
| SAFETY, HEALTH AND ENVIRONMENTAL POLICY | EPL 32-94 |  |
| EMP GUIDELINE | EPC 32-248 |  |
| WASTE MANAGEMENT PROCEDURE | EPC 32-245 |  |
| PROCEDURE FOR CLEARING VEGETATION AND MAINTENANCE WITHIN OVERHEAD POWERLINES | EPC 32-247 |  |
| HERBICIDES MANAGEMENT | ESKPBAAD4 |  |
| ESKOM STANDARD ON THE SAFE USE OF PESTICIDES AND HERBICIDES | ESKASAAL0 |  |
| RECOMMENDED HERBICIDES | DISTIZAB4 |  |

C4	Site Information

## C4.1 Information about the site at time of tender which may affect the work in this contract

### Figure 1: Substation Locality

The substation is located adjacent to the Omnia Fertilizer truck staging area. It is approximately 3.8km east of the Sasolburg CBD.

C4.1.2	Access limitations

Arrangements shall need to be made with the local CNC supervisor prior to any access to site.

C4.1.3	Ground conditions in areas affected by work in this contract Various Soil conditions to be determined by Contractors Civil Engineer C4.1.4	Hidden and Other Services within the Site

The risk for encountering hidden cables is high from inspections on site and thus the Contractor shall check and confirm any services prior to any construction activities commencing.

C4.1.5	Details of Existing Buildings / Facilities Which Contractor is required to Work On

Sasol Chem Substation Breaker Room.

| Title | Date or revision | Tick if publicly available |
| --- | --- | --- |
| General Specifications: |  |  |
| Health and Safety requirements |  |  |
| Environmental requirements |  |  |
| Site regulations and access control |  |  |
| Technical specifications: |  |  |

4. Constraints on how the Contractor Provides the Works

State any constraints on the sequence and timing of work and on the methods and conduct of work including the requirements for any work by the Employer. Also include any management related constraints, invoicing and payment procedures some of which have been inserted below as a minimum guide.

4.1 Meetings

Provide information about regular meetings to be held such as early warning and compensation event meetings (suggest weekly), safety and planning meetings.

4.2 Use of standard forms

Provide details of standard forms to be used by the Contractor in the administration of the contract, for example early warning and compensation event notifications.

## 4.3 Invoicing and payment

The Z clauses make reference to invoicing procedures stated here in this Works Information. Also include a list of information which is to be shown on an invoice.   The following text is provided as a guide; revise to suit actual requirements.

In terms of core clause 50 the Contractor assesses the amount due and applies to the Employer for payment.  The Contractor applies for payment with a tax invoice addressed to the Employer as follows:

______________________________________________________________________

The Contractor includes the following information on each tax invoice:

- Name and address of the Contractor

- The contract number and title.

- Contractor’s VAT registration number.

- The Employer’s VAT registration number 4740101508.

- The total Price for Work Done to Date which the Contractor has completed.

- Other amounts to be paid to the Contractor.

- Less amounts to be paid by or retained from the Contractor.

- The change in the amount due since the previous payment being the invoiced amount - excluding VAT, the VAT and including VAT.

- (Add other as required)

The Contractor attaches the detail assessment of the amount due to each tax invoice showing the Price for Work Done to Date for each item in the Price List for work which he has completed.

Add procedures for invoice submission and payment (e. g. electronic payment instructions)

4.4 Records of Defined Cost

In order to substantiate the Defined Cost of compensation events, the Employer may require the Contractor to keep records of amounts paid by him for people employed by the Contractor, Plant and Materials, work subcontracted by the Contractor and Equipment.  [See clause 11.2(5) and 63.2].  State in what form these records are to be kept and how accessed by the Employer.

### 4.5 Accelerated Shared Growth Initiative – South Africa (ASGI-SA)

If the ASGI-SA requirements are to be included in this contract specify constraints which Contractor must comply with after contract award in regard to any ASGI-SA requirements.  The ASGI-SA Compliance Schedule completed in the returnable tender schedules is reproduced here.  If ASGI-SA does not apply, delete this paragraph.

The Contractor complies with and fulfils the Contractor’s obligations in respect of the Accelerated and Shared Growth Initiative - South Africa in accordance with and as provided for in the Contractor’s ASGI-SA Compliance Schedule stated below

.

[Insert the agreed ASGI-SA Compliance Schedule here]

The Contractor shall keep accurate records and provide the Employer with reports on the Contractor’s actual delivery against the above stated ASGI-SA criteria.   [Elaborate on access to and format of records and frequency of submission etc.]

The Contractor’s failure to comply with his ASGI-SA obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.

### 4.6 BBBEE and preferencing scheme

Specify constraints which Contractor must comply with after contract award in regard to any Broad Based Black Economic Empowerment (B-BBEE) or preferencing scheme measures.

4.7 Facilities to be provided by the Contractor

State any requirements such as offices on site for the Employer.

4.8 Title to material from excavation and demolition

Read clause 70.2 then provide details as required.  Particularly relevant in demolition where substantial amounts of copper are involved.

4.9 Design by the Contractor

Paragraph 1 above will have outlined what work is to be designed by the Contractor (if any).  State here what procedures are required for the submission and acceptance of that design.

4.10 Cataloguing requirements by the Contractor

State whether cataloguing is applicable, if it is, reference the requirements for cataloguing that need to be satisfied by the Contractor (consult Procurement Instruction Number 1 of 2018 – Incorporating Cataloguing into the Procurement Environment, Unique Identifier 240-1289988974).

5.  Requirements for the programme

State whether a programme is required and, if it is, state what form it is to be in, what information is to be shown on it, when it is to be submitted and when it is to be updated. State what the use of the works is intended to be at their Completion as defined in Clause 11.2(1).

6. Services and other things provided by the Employer

Describe what the Employer will provide such as services (including water and electricity) and “free issue” Plant and Materials and equipment.

| Item | Date by which it will be provided |
| --- | --- |

C4:  Site Information

Site Information is information about the site at the time of tender which the tendering contractor needs to allow for in his rates and Prices. The information does not change after contract award, nor does it describe or specify anything which the Parties do during the contract. It is only referred to during administration of the contract if the Contractor encounters conditions which are different to those described here. The Contractor will then make a comparison between actual conditions encountered and those described here in his assessment of any additional cost or time he may need to be compensated for in order to complete the works. Disputes about the difference between the effects of conditions encountered and those which the Contractor allowed for in his Prices will be minimised if the information given here is complete and relevant. If no information is given the tendering contractor will need to guess what he may encounter thus tendering higher Prices to allow for conditions that may not even exist.

# C4.1: Information about the site at time of tender which may affect the work in this contract

## 1. Access limitations

State if there is any physical, time or other “third party” constraint associated with gaining access to and doing work on the site that may not be immediately apparent from an inspection of the site.

## 2.  Ground conditions in areas affected by work in this contract

If earthworks are included in the Scope of Work, provide details of the ground conditions the Contractor is likely to encounter when doing the work. This could vary from indicating where a test pit has been opened up for the Contractor to make his own observations to providing full borehole logs and associated geotechnical report.

## 3.  Hidden and other services within the site

Provide details of underground or other hidden services which the Contractor may encounter whilst doing the work. Instructions about how to deal with them if encountered should be included in the Works Information.

## 4.  Details of existing buildings / facilities which Contractor is required to work on

If work is to be carried out on existing buildings or facilities Site Information would be the ‘as-built drawings’ of those buildings or facilities. If these are not a correct statement or not available other means of describing the existing buildings or facilities would have to be used, such as providing photographs

Available from Engineering Contract Strategies Tel 011 803 3008, Fax 086 539 1902 or www.ecs.co.za

Except those actions which can only be done by the Employer as a Party to the contract.

If June 2005 Edition applies, delete April 2013 and insert June 2005

State whether attached as a ‘PDF’ file in terms of Eskom’s licence, or to be obtained from Engineering Contract Strategies Tel 011 803 3008, Fax 086 539 1902 or www.ecs.co.za.

Available from Engineering Contract Strategies Tel 011 803 3008, Fax 086 539 1902 or www.ecs.co.za.