## Template Identifier
LOW VOLTAGE INDUCTION MOTORS TECHNICAL SCHEDULE A&B TEMPLATE | Template Identifier | 240-77100923 (Rev 3)
| Document Identifier | xxx-xxx
| Revision | x.x
| Next Review Date | 2029-02-01
Generation Engineering

## LV Induc. Motor Tech. Schedule
LOW VOLTAGE INDUCTION MOTORS TECHNICAL SCHEDULE A&B TEMPLATE
|  | Project Name: | Supply and delivery of ACC fan motors
Project No:
PLANT DESCRIPTION (e.g. Boiler, Turbine, Coal overland, etc.) |  |  | Condensate Plant
APPLICATION (e.g. Fan, Pump, Mills, Conveyor, etc.) |  |  | Fan Motor
ITEM | DESCRIPTION |  | UNITS | ESKOM or SUPPLIER |  | ESKOM Comments | SUPPLIER Comments
2 | Power Supply |  | UNITS | ESKOM | SUPPLIER | ESKOM Comments | SUPPLIER Comments
2.1 | Normal Supply |  |  | Schedule A | Schedule B | Eskom Spec - 240-57617975
2.101 | Supply Voltage, 3-phase, ± 5% (e.g. 380V, 400V, 525V, 660V and 690V) |  | V | 525 ± 5% |  | Tender Phase (Section 3.3.1)
2.102 | Supply frequency, 50Hz ± 2% |  | Hz | 50 ± 2% |  | Tender Phase
2.103 | Voltage unbalance: Negative sequence voltage up to 2 % of positive sequence voltage (Vp). |  | % | 2% |  | Tender Phase
2.104 | Voltage harmonic distortion |  | % | <= 5%. |  | Tender Phase
2.2 | Abnormal power supply (prevailing simultaneously for up to 6 hours)
2.201 | Supply Voltage, 3-phase, ± 10% (e.g. 380V, 400V, 525V, 660V and 690V) |  | V | 525 ± 10% |  | Tender Phase
2.202 | Supply frequency, 50 Hz ± 2% for 80 minutes |  | Hz | 50 ± 2% |  | Tender Phase
2.203 | Voltage unbalance: Negative sequence voltage up to 3 % of nominal positive sequence voltage. |  | % | 3% |  | Tender Phase
2.204 | V/F ratio < 1.1pu |  | pu | <= 1.1 |  | Tender Phase
2.3 | Transient - voltage within 10% of nominal within 3 seconds after the transient:
2.301 | Complete loss of supply for 0.2 seconds |  | s | 0.2 |  | Tender Phase
2.302 | Voltage depression up to 85% of nominal for up to 60 second |  | % | 85% for 1minute |  | Tender Phase
2.303 | Voltage depression up to 75% of nominal for up to 1 second |  | % | 75% , 1second |  | Tender Phase
3 | Environment |  | UNITS | ESKOM | SUPPLIER | ESKOM Comments | SUPPLIER Comments
3.01 | Altitude above see level (e.g. 1000, 1600) |  | m | 820 |  | Tender Phase
3.02 | Average temperature |  | ºC | 38 |  | Tender Phase
3.03 | Maximum temperature |  | ºC | 42 |  | Tender Phase
3.04 | Minimum temperature |  | ºC | 20 |  | Tender Phase
4 | Motor General Information
4.01 | Applicable SANS standard |  | Code | SANS60034, SANS 1804 |  | Tender Phase
4.02 | Applicable Eskom Specification |  | Number | 240-57617975 |  | Tender Phase
4.03 | Motor manufacturer |  | Name | Supplier to Provide |  | Tender Phase
4.04 | Motor manufacturer reference code/serial number |  | Code | Supplier to Provide |  | Tender Phase
4.05 | Fabrication place |  | Name | Supplier to Provide |  | Tender Phase
4.06 | Motor life expectancy |  | yrs | >=20 |  | Tender Phase
4.07 | Motor colour |  | SANS 1091 | G29 - Light Grey |  | Tender Phase
4.08 | Local testing facility |  | Name | Supplier to Provide |  | Tender Phase
5 | Motor Electrical Details (Refer to Section 3.1.2 of 240-56357518)
5.1 | Motor Rating
5.101 | Rated output power |  | kW | 280 |  | Tender Phase
5.102 | Supply voltage (e.g. 230V, 380V, 400V, 525V, 660V and 690V) |  | V | 525 |  | Tender Phase
5.103 | Frequency (e.g. 50 or 60) |  | Hz | 50 |  | Tender Phase
5.104 | Full load current |  | A | 365 |  | Tender Phase
5.105 | Rated Speed |  | RPM | 1485 |  | Tender Phase
5.106 | International Efficiency class code (e.g., IE1, IE2, IE3) |  | Code | IE3 |  | Tender Phase
5.107 | Winding connection |  | Star / Delta | Delta |  | Tender Phase
5.108 | Duty-class (e.g. S1, S2, S3, etc. as per IEC 60034-1) |  | Code | S1 |  | Tender Phase
5.109 | Utilization factor (Load power at duty point/motor rated power) |  | % | >=75%,=<90% |  | Tender Phase
5.11 | Ex rating (required for Zone 0-2,20-22 Classification) (e.g. Zone 22 (dust), Zone 2 (gases) |  | Yes / No | No |  | Tender Phase
5.111 | Ex Code (e.g. Ex td A22 T125ºC IP65 (dust), Ex na II T3 (non-sparking), Ex d/de (Flameproof) |  | Code | N/A |  | Tender Phase
5.2 | Motor Performance Guarantees
5.201 | Full load torque |  | Nm | 1800 |  | Tender Phase
5.202 | Locked rotor torque |  | pu | 3600 |  | Tender Phase
5.203 | Pull-up torque |  | pu | 2880
5.204 | Breakdown torque |  | pu | 3600 |  | Tender Phase
5.205 | Locked rotor current (<9pu for IE3) |  | pu | 6.5 |  | Tender Phase
5.206 | Efficiency at 100% Loading |  | % | 96 |  | Tender Phase
5.207 | Efficiency at 75% Loading |  | % | 96 |  | Tender Phase
5.208 | Efficiency at 50% Loading |  | % | 95 |  | Tender Phase
5.209 | Power factor at 100% Loading |  | % | 85 |  | Tender Phase
5.21 | Power factor at 75% Loading |  | % | 83 |  | Tender Phase
5.211 | Power factor at 50% Loading |  | % | 78 |  | Tender Phase
5.3 | Motor parameters (for motors 200kW and above)
5.301 | X/R Ratio |  | % | Supplier to Provide |  | Contract Phase
5.302 | Stator Resistance @ Standstill (slip = 1) |  | W | Supplier to Provide |  | Contract Phase
5.303 | Stator Reactance @ Standstill (slip = 1) |  | W | Supplier to Provide |  | Contract Phase
5.304 | Rotor Resistance @ Standstill (slip = 1) |  | W | Supplier to Provide |  | Contract Phase
5.305 | Rotor Reactance @ Standstill (slip = 1) |  | W | Supplier to Provide |  | Contract Phase
5.306 | Stator Resistance @ Full Load |  | W | Supplier to Provide |  | Contract Phase
5.307 | Stator Reactance @ Full Load |  | W | Supplier to Provide |  | Contract Phase
5.308 | Rotor Resistance @ Full Load |  | W | Supplier to Provide |  | Contract Phase
5.309 | Rotor Reactance @ Full Load |  | W | Supplier to Provide |  | Contract Phase
5.31 | Full Load Slip |  | % | Supplier to Provide |  | Contract Phase
5.311 | Specified Temperature |  | ºC | Supplier to Provide |  | Contract Phase
5.312 | Magnetic Reactance (Xm) |  | W | Supplier to Provide |  | Contract Phase
5.313 | Magnetic Resistance (Rm) |  | W | Supplier to Provide |  | Contract Phase
6 | Motor Thermal Details (Refer to Section 3.1.2 of 240-56357518)
6.1 | Temperature rise
6.101 | Stator winding insulation class (Minimum class F) |  | Name | F or H |  | Tender Phase
6.102 | Stator winding temperature rise |  | K | 80 |  | Tender Phase
6.2 | Allowable locked rotor time (s)
6.201 | Hot |  | s | Supplier to Provide |  | Contract Phase
6.202 | Cold |  | s | Supplier to Provide |  | Contract Phase
6.3 | Performance and Thermal Capacity
6.301 | Run-up time at 100% of rated voltage |  | s | Supplier to Provide |  | Contract Phase
6.302 | Run-up time at 90% of rated voltage |  | s | Supplier to Provide |  | Contract Phase
6.303 | Thermal time constant |  | s | Supplier to Provide |  | Contract Phase
6.304 | Cooling time constant |  | s | Supplier to Provide |  | Contract Phase
6.305 | Number of starts from Hot, within an hour |  | s | 2 |  | Contract Phase
6.306 | Number of starts from cold, within an hour |  | s | 3 |  | Contract Phase
7 | Mechanical Details (Refer to Section 3.1.3 of 240-56357518)
7.1 | Motor insulating system
7.101 | Method of stator winding Impregnation |  | Name | VPI/CRF |  | Tender Phase
7.102 | Squirrel cage rotor type (e.g. die cast aluminium or copper or fabricated rotor) |  | Name | Supplier to Provide |  | Tender Phase
7.2 | Enclosure and cooling
7.201 | Enclosure - Degree of protection (IP Code) (General IP55, Dust - IP65) |  | Code | IP55/65 |  | Tender Phase
7.202 | Cooling Method (IC code) |  | Code | IC411 |  | Tender Phase
7.3 | Bearings
7.301 | Bearing type (e.g. Ball or Roller or Sleeve) |  | Name | Roller and Ball |  | Tender Phase
7.302 | Lubrication type (oil or grease) |  | Name | Grease |  | Tender Phase
7.303 | Lubrication interval |  | hrs | >= 4000 |  | Tender Phase
7.304 | Bearing life (40 000hrs for <200kW, 100 000hrs for >200kW) |  | hrs |  |  | Tender Phase
7.4 | Motor Size
7.401 | Frame size |  | Code | D355LD |  | Tender Phase
7.402 | Shaft diameter and length (mm) |  | mm | 110/210
7.403 | Rotor Moment of inertia |  | kgm² | Supplier to Provide |  | Tender Phase
7.404 | Motor total mass |  | kg | 1960 |  | Tender Phase
7.5 | Vibration and Noise
7.501 | Bearing vibration limits |  | mm/s | 1.6 |  | Tender Phase
7.502 | Noise level |  | dB | <85 |  | Tender Phase
8 | Accessories (Refer to Section 3.1.4 of 240-56357518)
8.1 | Temperature Measuring Devices
8.101 | Stator Winding Embedded Temperature Detectors (ETD) installed |  | YES/NO | Yes |  | Tender Phase
8.102 | Stator Winding ETD Type (Thermistors or PT100 or thermocouples) |  | Name | Thermistor and PT100 |  | Tender Phase
8.103 | Number of Stator winding ETDs |  | Number | 1-phase and 2-phase |  | Tender Phase
8.104 | Bearing ETD Installed |  | YES/NO | Yes |  | Tender Phase
8.105 | Bearing ETD Type (thermocouples or PT100 situated in the DE and NDE bearing). |  | Name | PT100 |  | Tender Phase
8.106 | Bearing thermocouples or PT100 situated in the DE and NDE bearing (if required). |  | Number | 2-phase |  | Tender Phase
8.107 | Separate auxiliary box for the temperature measuring devices. |  | YES/NO | Yes |  | Tender Phase
8.2 | Space Heaters (see 3.1.4.2)
8.201 | Space heaters |  | YES/NO | No |  | Tender Phase
8.202 | Power rating of the space heaters to operate on 230Vac. |  | kW | NA |  | Tender Phase
8.203 | Separate auxiliary box for the heaters. (see 3.1.4.2b) |  | YES/NO | NA |  | Tender Phase
9 | Interface to Plant
9.01 | Motor mounting (Horizontal / Vertical) (Foot/Flange) |  | Name | IM V1 (vertical flange) |  | Tender Phase
9.02 | Rotation (viewed on motor drive shaft) with U- V- W |  | Name | Supplier to Provide |  | Tender Phase
9.03 | Suitable lifting devices |  | Number | 2 |  | Tender Phase
9.04 | Maximum cable size that can fit on the terminal box |  | mm2 | Supplier to Provide |  | Tender Phase
9.05 | Direction of cable entry |  | Describe | left and right |  | Tender Phase
9.06 | Cable type |  | Code |  |  | Tender Phase
9.07 | Cable size |  | mm2 | Supplier to Provide |  | Tender Phase
9.08 | Cable outside diameter |  | mm | Supplier to Provide |  | Tender Phase
10 | Station Limitations
10.01 | Maximum Motor Mass (Station limit) |  | kg | 1950 |  | Supplier not to exceed the limit
10.02 | Maximum Allowed Overall Motor Height (Station limit) |  | mm | 1580 |  | Supplier not to exceed the limit
10.03 | Maximum Allowed Overall Motor Breadth (Station limit) |  | mm | Supplier to Provide |  | Supplier not to exceed the limit
11 | Drawings
11.001 | Outline drawing reference number |  | Number | Supplier to Provide |  | Tender Phase
11.002 | Power winding schematic diagrams and Auxiliaries schematic diagrams (PT100s, thermistor and heaters) reference number |  | Number | Supplier to Provide |  | Contract Phase
11.1 | Motor Curves
11.101 | Torque-speed curves plotted over the driven machine torque-speed curve at rated Voltage reference number |  | Number | Supplier to Provide |  | Contract Phase
11.102 | Current-speed curves at rated voltage reference number |  | Number | Supplier to Provide |  | Contract Phase
11.103 | Efficiency and Power factor vs. load curves at rated voltage reference number |  | Number | Supplier to Provide |  | Contract Phase
11.104 | Thermal limit curves reference number for Motors =>55kW reference number |  | Number | Supplier to Provide |  | Contract Phase
11.2 | Manuals and Test Reports
11.201 | Inspection and Test Plan for Motors for motors =>200kW |  | Number | Supplier to Provide |  | Contract Phase
11.202 | Required performance test certificates and Routine certificates (for all motor sizes) |  | Number | Supplier to Provide |  | Contract Phase
11.203 | Installation, operating and maintenance manual (for all motor sizes) |  | Number | Supplier to Provide |  | Contract Phase
Note on C64: Eskom: Required for load flow studies
Note on C85: Eskom: Required for protection
Note on C131: Eskom: Cable info many not be available at tender
Note on C147: Marubini Manyage: Motors >=200kW will be type tested and witnessed
Note on G7: Marubini Manyage: Eskom or contractor to fill depending on the type and phase of the project
Note on H9: Marubini Manyage: Contractor to confirms motor capability to the power supply provided
Note on H25: Marubini Manyage: Contractor to confirms motor capability to the power supply provided

## Deviation List
LOW VOLTAGE INDUCTION MOTORS TECHNICAL SCHEDULE A&B TEMPLATE
|  | Project Name: |  |  | Project No:
DEVIATION LIST
1. Any deviations/modifications/alternatives offered to this standard specification is listed below with reasons for the departures. 2. No deviations/modifications/alternatives offered to the standard is recognized unless listed on this schedule.
Item | Document Reference # | Document Title | Clause # | Proposed Deviation
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
2.1