## A&B Schedules
Technical Schedules A and B for
Inverter
Schedule A: Purchasers specific requirements
Schedule B: Guarantees and technical particulars of equipment offered
1 | 2 |  |  | 3 | 5
Item | Description |  |  | Schedule A | Schedule B
1 | Product Information
1.1 |  | OEM | OEM Name | xxxxxxxxxx
2 | Inverter Characterisitics
2.1.3 |  | Inverter type | --- | Hybrid
2.1.4 |  | Maximum conversion efficiency | % | ≥ 97
2.1.5 |  | Operating temperature range (without derating within this range). Sun shade shall be installed. Concept shall be briefly explained in inverter concept within tender. | °C | -10 to +50
2.1.6 |  | Maximum DC voltage | V | 1000
2.1.7 |  | Connection phases |  | Three-Phase
2.1.8 |  | Internal transformer | Yes/No | No
2.1.9 |  | Frequency | Hz | 50
2.1.10 |  | Total Harmonic Distortion | % | ≤ 3
2.1.11 |  | Nominal AC power per inverter type | kVA | ≥ 10
2.1.12 |  | IP for inverter installed outdoor (EN 60529) |  | ≥IP65 or better
2.1.13 |  | Cooling concept |  | Designed for installation and operation in conditions such as high humidity and corrosive salt air.
2.1.14 |  | Controllability of inverter output per remote control/energy management system. |  | Dynamic adjustable
2.1.15 |  | Earthing concept |  | Earthing according to installation requirements of PV module OEM.
2.1.16 |  | Multiple MPPT functionality |  | Required
2.1.17 |  | String failure detection |  | Required
2.1.18 |  | DC overvoltage protection |  | Required
2.1.19 |  | Surge protection |  | Required
2.1.20 |  | Total Harmonic Distortion | % | ≤ 3
2.2 | · | Product Warranty and Performance Guarantee
2.2.1 |  | Product warranty | Years | 10
2.2.3 |  | Service life | Years | ≥20
3 | Minimum Certificates and Standards
3.1 |  | SANS 60364-7-712:2018 - Low voltage electrical installations. Part 7-712: Requirements for special installations or locations - Solar photovoltaic (PV) power supply systems. | Present certification / conformity declaration | Required
3.2 |  | IEC 62109 Safety of Static Inverters | Present certification / conformity declaration | Required
3.3 |  | IEC 61727 Characteristics of the Utility Interface | Present certification / conformity declaration | Required
3.4 |  | IEC 62116 Testing procedure of Islanding Prevention Methods for Utility-Interactive Photovoltaic Inverters | Present certification / conformity declaration | Required
3.5 |  | IEC 62103 Electronic equipment for use in power installations | Present certification / conformity declaration | Required
3.6 |  | SANS 62109-2:2020 Safety of power converters for use in photovoltaic power systems - Part 2: Particular requirements for inverter | Present certification / conformity declaration | Required
3.7 |  | IEC 61000-6-1/2 - EMC Immunity | Present certification / conformity declaration | Required
3.8 |  | IEC 61000-6-3/4 - EMC Emission | Present certification / conformity declaration | Required
3.9 |  | NRS 097-2-1:2024 Edition 3 Small-scale Embedded Generation, Utility Interface | Present certification / conformity declaration | Required
3.10 |  | SANS 60146-2:1999 Semiconductor convertors - Part 2: Self-commutated semiconductor converters including direct d.c converters | Present certification / conformity declaration | Required
3.11 |  | Other standards considered relevant by the Bidder | Present certification | To be provided by the Bidder
4 | Documentation for Acceptance of PV Modules
3.1 |  | Detailed technical specifications | Present documentation | Required
3.2 |  | Product information catalogue | Present documentation | Required
3.3 |  | Installation manual | Present documentation | Required
3.4 |  | Summary of the product's cleaning strategy | Present documentation | Required
3.5 |  | Calculations for ensuring electrical compatibility between the inverters and the modules | Present documentation | Required
3.6 |  | Operating and maintenance manual | Present documentation | Required
3.7 |  | Project References – Highlight at least three projects where an inverter with a minimum capacity of 3kW was installed. | Present documentation | Required
BIDDER's SIGNATURE
Name (Print) |  |  |  | Company Name
Sign |  |  |  | Date

## Deviation Schedule
Deviation schedule
Inverter
Deviations offered to this specification shall be listed below with reasons for deviation. This includes deviations on the AB Schedules, Drawings and Test Reports. In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective that that specified by Eskom.
Item | Clause | Description of Deviation
BIDDER's SIGNATURE
| Name (Print) |  | Company Name
| Sign |  | Date

## Test Schedule
Test Report Schedule
Inverter
Important! Check your submission to ensure that the specific test result for the specific tests stipulated can be found in the submission. Missing tests will affect the technical result.
| 1 | 2 | 3 | 4
| Item | Description | Specification | Report No.
| 1 | Load transfer test | SANS 62109-2:2020
| 2 | Cooling system failure – Blanketing test | SANS 62109-2:2020
| 3 | Electrical ratings tests | SANS 62109-2:2020
| 4 | Visual inspection | SANS 60146-2:1999
| 5 | Checking auxiliary devices | SANS 60146-2:1999
| 6 | Insulation test | SANS 60146-2:1999
| 7 | Checking the protective devices | SANS 60146-2:1999
| 8 | Light load and functional test | SANS 60146-2:1999
| 9 | Rated output test | SANS 60146-2:1999
| 10 | Overcurrent test | SANS 60146-2:1999
| 11 | Temperature rise test | SANS 60146-2:1999
| 12 | Power loss determination | SANS 60146-2:1999
| 13 | Measurement of THD for voltage and current | SANS 60146-2:1999
| 14 | Measurement of power factor | SANS 60146-2:1999
| 15 | Checking of automatic control | SANS 60146-2:1999
| 16 | Short circuit test | SANS 60146-2:1999
| 17 | Measurement of ripple voltage and current | SANS 60146-2:1999
| 18 | Measurement of audible noise | SANS 60146-2:1999
| 19 | Immunity test | SANS 60146-2:1999
BIDDER's SIGNATURE
Name (Print) |  |  |  | Company Name
Sign |  |  |  | Date