Questions and Answers

1.Hi Limpho,

Hope this email finds you well, trust your morning is great.

Kindly advise when the Documents for the below Tender will be made available.

1.Good day

All documents were uploaded on both national treasury and Eskom tender bulletin.  Just went in on my side and it shows that are uploaded

2. **Clarification required for**

**Items 14 - 18**:  The Eskom code **BVX04LCV** ends with the letter  “ V” suggesting **Red Stripe(FR)**  yet the short description speaks of “LOW HALOGEN W/BLUE STRIPE COVERIN”- Please confirm if this is **Red Stripe(FR)** or **Blue Stripe(LH)** on the Sheath.

2. The “ V “ represents the outer sheathing “offering mechanical protection and flame retardance”

Flame Retardant PVC (FR PVC) and Low Halogen Emission PVC (often part of FRLSH or LSZH cables),

**Blue strip as specified in the material description**.

3. APPENDIX B: Items 34-38 Rubber Cables there is a requirement for Trailing cables rated at 1000V, however the description requires HO7 cables. Our HO7 cables are rated at 450/750V, our LV Trailing cables are rated at 640/1100V. Please clarify which is required.

3. **Response** 1 . item 34-38 appendix B, cable spec has specified HO7 RN-F , which is rated for 450/750V, while required maximum required voltage is 1000V as, The code should have been HO7 BN-F to accommodate 1KV voltage. The 640/1100 V cable is acceptable on the bases of required maximum required voltages.

1. APPENDIX B: Items 19 & 30 requires armoured cables however clause 3.4.3.4 requires unarmored cables. Please clarify which is required.

4. **Response 2**.  The cables items 19 & 30 are considered under medium voltage cables , based on Generation Requirements for Control and Power Cables for Power Stations Standard : 240-56227443

3.3.2.1 General requirements for MV cables, Subsection 3.3.2.4 Armour

**a) Single-core cables shall be unarmoured.**

3.3.3 Low voltage power cables

3.3.3.1 General requirements for Low Voltage cables, Subsection 3.3.3.7 Armouring

a) Single-core cables shall have aluminium wire armour, unless otherwise specified.

1. My question was for sme who rely on financial backup from credit providers, can we submit a letter of intent (financial guarantor letter) alongside the financial statement

5. Yes, they can do that.

6. hould we price each product separately, or calculate pricing on the total order value?

6. They must calculate as per below:

* Quantity of the item multiple by the rate = total amount.
* Do the same process to all items until the last item.
* After they are done, they must add all item TOTAL AMOUNT to get to thier tender amount.
* They must also propose their CPA table should they are not happy with Eskom’s CPA table
* If they did not propose CPA table, their prices will be fix for the duration of the contract.

7. Can I please have the Technical Schedule A and B for the above-mentioned tender.

7. **Response 3.** There is no schedule A & B required on the tender. Appendix B is what is used for GVL PS power cables specification