## Eval Criteria
Technical Returnables Schedule
Spec. clause number | Description | Score | Returnable | Schedule B (Supplier’s compliance statement) | Supplier’s Reference/Comment (Supporting evidence)
1 | Functionalities to ensure comprehensive control, efficient operation, and robust performance | 10
1.1 | Manual Control: The microgrid system must provide the capability for manual control, allowing the operator to intervene directly when necessary. This is essential for testing different scenarios and making real-time | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.2 | Voltage Control (Volt-var Control): The system must be equipped with voltage control capabilities to maintain stable voltage levels across the microgrid. This involves adjusting reactive power to manage voltage variations, ensuring that all connected loads receive power within the specified voltage range. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.3 | Frequency Control: Maintaining the frequency of the AC supply within acceptable limits is critical for the stability and reliability of the microgrid. The system shall include frequency control mechanisms to adjust the power output and balance generation with consumption, preventing frequency deviations. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.4 | P-Control (Curtailment): The microgrid must manage and curtail power output to match demand and prevent overloading. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.5 | Load Management: The system must dynamically adjust load consumption based on real-time data read from the load metres, ensuring optimal performance and preventing using the batteries beyond optimum limits. This helps in maintaining a stable and reliable power supply to all connected loads. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.6 | Switching: The microgrid includes advanced switching capabilities (switching time < 20ms) to seamlessly transition between different power sources. This ensures a continuous and reliable supply of electricity, even when switching from one generation source to another. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.7 | Metering and Revenue Collection: The system shall feature advanced metering solutions to accurately measure energy consumption at various points within the microgrid. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.8 | Short-Term Forecasting: It shall be equipped with short term forecasting capability and use the resource forecast to optimise its dispatch strategy between the available energy resources in the facility. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.9 | Programmable Load: The microgrid shall include a programmable load feature that can emulate different load classes and profiles. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
1.10 | Economic Dispatch: the system must be equipped with capability that will make it possible to programme it to do economic dispatch based on user inputs. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
2 | Solar PV Requirement--- The solar PV panels will be installed on a ground-mounted support structure, providing a stable and accessible platform for the array. To maximize energy capture, the PV system will include single axis tracking capability, allowing the panels to follow the sun's movement throughout the day. The required PV power output for this facility is 30kWac. | 8
2,1 | Single axis tracking capability | 4 | State Compliance & Provide Evidence in the Preliminary Design Report
2,2 | Ground mounted design | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
2,3 | 30kWac Output | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
3 | Battery Energy Storage Requirements---Batteries are required to charge from the PV and from the wind turbines’ generation outputs. The usable BESS capacity required for this microgrid is 60kWh. Thus, the successful respondent must design the capacity (constructed) such that the usable output is 60kWh. The design must account for manufacturer’s suggested DoD. | 8
3,1 | 60kWh usable capacity | 4 | State Compliance & Provide Evidence in the Preliminary Design Report. Must include Single Line Diagrams.
3,2 | Manufacturer's DoD consideration in the design | 2 | State Compliance & Provide Evidence in the Preliminary Design Report. Must include Single Line Diagrams.
3,3 | Can charge from Solar PV / wind generator | 2 | State Compliance & Provide Evidence in the Preliminary Design Report. Must include Single Line Diagrams.
4 | Wind Turbine Generator Requirements---The turbines are required to provide power generation during the night-time and when the solar resource is scarce. The output of the turbines shall be 30kWac. The functionality to control power output/curtailment in line with the load demand shall be made available. | 8
4,1 | 30kWac Output | 4 | State Compliance & Provide Evidence in the Preliminary Design Report
4,2 | Output power control (curtailment) | 4 | State Compliance & Provide Evidence in the Preliminary Design Report
5 | Power Conversion System (PCS) Requirements: | 10
5,1 | The power conversion system shall convert the combine output of the PV and BESS from DC to AC. In addition, the power conversion system must allow the BESS to charge from the PV / WTG. | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
5,2 | It must provide volt-var support and frequency control support. | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
5,3 | The power conversion system shall have a capacity of 30kW. | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
5,4 | The Power Conversion System must adopt a modular design. | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
5,5 | The solution shall be able to take set-points and provide outputs as per the set-points. | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
6 | Programmable Load Requirements: The programmable load will complete the microgrid by representing the customers. It shall be equipped with capability to take the following load profiles: | 6
6,1 | 24-hour profile | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
6,2 | 8760-hour profile | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
6,3 | Generalised seasonal profiles (typical summer, winter day, etc), week -day and weekend-day profiles | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
6,4 | Data resolution: 15 minutes data with option to make it 1 hour. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
6,5 | Input data: apparent power (kVA); real power (kW); reactive power (kvar); power factor (The input data will be provided in MS Excel spreadsheets.) | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
6,6 | This load must be capable of maximum demand of 30kW at 0.8 power factor (lead/lag). | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7 | Network Unit Requirements: The network will carry sensors, and smart meter services. | 12
Network Switch：
7,1 | Dual-power supply redundancy design and Supports PoE+. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7,2 | Supports at least 8 x 10/100/1000Base-T Ethernet ports, 2 x 10GE SFP+ ports. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7,3 | Fault-free operation under strong magnetic interference, meeting the requirements of IEEE1613. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet. IEEE1613 compliance certificate.
7,4 | Complies with the requirements of the strict environmental standard IEC61850-3 for substations. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet. IEC61850-3 compliance certificate.
Network Router
7,5 | Supports at least 2 x RS485/RS232, 3 x GE electrical ports, 2 x GE SFP ports | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7,6 | long-term operating at -10°C to 50°C | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7,7 | 5G, LTE TDD, LTE FDD, WCDMA | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7,8 | Complies with the requirements of the strict environmental standard IEC61850-3 for substations. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
AC collection unit
7,9 | Supports the IEC 62056-46 or IEC 61850-3 protocol. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet. IEC 62056-46 or IEC 61850-3 compliance vertificate.
7,10 | Supports analogue quantity acquisition functions such as voltage and current, and can measure voltage, current, power, power factor, etc. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
7,11 | Accuracy: 0.2S active power level, 2 reactive power level. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
HPLC/G3PLC communication unit:
7,12 | A maximum of 2000 STAs and 15-level trunks are supported. To be modular design and support plug & play. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
8 | Protection Requirements: Key components of the facility shall be equipped with circuit breakers/smart meters that can be controlled locally or remotely. The role of such breakers/meters is to provide overcurrent fault protection during fault condition, detection and isolation of faulty sections of the facility and auto-reclosing after the fault was cleared. The state of these breakers/meters(on/off) must be viewable from the office and the system must allow manual changes to switch state. The fault current rating of the protection breaker/meters shall be calculated as part of the design by the successful bidder.
8
8,1 | Circuit breakers/smart meters that can be controlled locally or remotely | 2 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
8,2 | Provide overcurrent fault protection during fault condition | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
8,3 | Detection and isolation of faulty sections of the facility | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
8,4 | Auto-reclosing after the fault was cleared | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
8,5 | The state of these breakers/meters(on/off) must be viewable from the office | 2 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
8,6 | The fault current rating of the protection breaker/meters shall be calculated as part of the design by the successful bidder | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9 | Monitoring and Control Functionality Requirements: The monitoring and control functionality will show the physical working status of each entity. It will provide all the information about the facility and will be displayed in the dashboard format in the Office Room. The following minimum functionalities are applicable: | 12
9,1 | Configuration/status (on/off) of devices in the field. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,2 | Keeping a record and history of replaced devices. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,3 | Device data collection & processing. Reporting and Analytics. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,4 | Two-way communication capability (Remote connect\disconnect) | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,5 | On demand request and response capabilities. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,6 | Outage and Power Quality analysis. Demand response management. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,7 | Remote firmware upgrade of field devices. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,8 | Ability to Maintain system time synchronization across all devices to ensure accuracy of data. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,9 | Ability to provide/display Output of Generation from each component (BESS, PV, Wind). | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,10 | Ability to Collect and analyse the power consumption data of end user/load for the purposes of: power consumption monitoring, load management, and line loss analysis. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,11 | Server minimum requirement, 448vCPU, 1792GB DDR4, 35TB Usable Capacity configured with SSD Disk in total, 2*10GE SFP+ each node | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
9,12 | Network requirements, at least two 48*10G SFP+ and 6*100G QSFP28 data center switches, at least two gateways with the SIM communication function and secure remote access capability | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
10 | Office Room Signals: The control room is to be equipped to monitor and report a wide range of signals, ensuring comprehensive oversight and management of the microgrid. It must be equipped with the following | 10
10,1 | 65-inch infrared screen: interactive smart whiteboard for training (interactive touch panel; video conferencing; speaker; microphone; web-camera), | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
10,2 | Screen to support voice tracking and auto framing function, | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
10,3 | Compatible with Microsoft Teams, Zoom and other meeting software | 1 | State Compliance & Provide Evidence in the Preliminary Design Report, Component datasheet
10,4 | Manual input controls for the facility (for switching, setpoints, etc) | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
10,5 | Control Room Container size specifications: 20ft | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
10,6 | Control room container Inner dimensions (mm) (BxWxH): 6058x3100x3100 | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
10,7 | Control room container air conditioning type: Integrated fluorine pump air conditioner + dual system backup | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
10,8 | Control room container fire extinguishing method: Heptafluoropropane automatic fire extinguishing system. Smoke sensor and temperature sensor (standard configuration), fire alarm system, emergency manual button triggering, and fresh air and smoke exhaust system after a disaster | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
10,9 | Monitors: Supports local and remote web page access and provides the alarm function. | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
10,10 | Provide a separate enclosure to house batteries, power conversion system and other sensitive electronic and electrical equipment.This is to protect sensitive equipment from weather elements. It shall have effective fire detection and protection, and effective cooling mechanism. The enclosure must not exceed the dimensions (mm) (BxWxH): 1000x1000x2000 | 1 | State Compliance & Provide Evidence in the Preliminary Design Report
11 | Hybrid Wind and Solar PV Microgrid Research Facility Preliminary Design: Overall Generating Capacity | 8
11,1 | System Design parameters | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
11,2 | High level plant layout drawing | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
11,3 | Detail how metering, data housing and display, and analysis is going to be incorporated. | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
11,4 | Detail how the overall system is going to operate as a single unit | 2 | State Compliance & Provide Evidence in the Preliminary Design Report
| Total | 100