## Activites Tables
Steps # | Activities for Eskom Technical Assessment Team
1 | Find Tables A3.1, A3.2, A3.3
2 | Complete Table 3 Mandatory Criteria
3 | Proceed to evaluate Tenderer that meets Table 3 Mandatory Criteria
4 | Evaluate Technical File of Tenderer
5 | Review submission for Table A3.1 and score Table A3.2 for the submitted ADSS - link with Type Test report submitted
6 | Review Indexed Factory File submission and score Table 6
7 | Review Data Sheets information submitted for the ADSS and score
8 | Review PLSCADD information submitted for the ADSS and score
9 | Consolidate Scores for Desktop evaluation from steps 6, 7 and 8 above
10 | Feedback draft report to Commercial indicating which Tenderers have passed Desktop evaluation
11 | Commercial to inform tenderer and indicate dates for Factory visits
12 | Factory Visits by Cross-functional team
13 | Final Report completed
Step # | Activities and Submission Summary for Tenderers
1 | Submit a properly indexed Technical File
2 | Submit completed Table A3.1 - A/B Schedules for ADSS offered
3 | Submit completed Table A3.2 - TYPE TESTS status
4 | Submit completed Table A3.3 - FACTORY FILE index completed
5 | Submit most recent TYPE TESTS for the ADSS offered
6 | Submit most recent DATA SHEETS for the ADSS offered
7 | Submit most recent PLSCADD information for the ADSS offered
8 | Submit indexed file with Factory Information correlating to Table A3.3

## Mandatory Criteria Table A3.0
ADSS Cable Mandatory Criteria | Comply (Yes/No)
A and B Schedules completed to Eskom requirements for the ADSS cables provided in English? NRS 078-1 format (Complete Table A3.1)
Stated which Type tests are submitted and which will be provided during Factory Evaluation. Minimum Threshold score for Type Tests submitted is 80%. (Complete Table A3.2)
File of information supplied for Table A3.3 for Factory Evaluation
Table #1 Mandatory Criteria | List of A/B schedules required
Table #2 Mandatory Criteria | List of Type Tests
Table #3 Mandatory Criteria | List of items for FAT

## ADSS Table A3.1
Table A3.1 Mandatory Criteria - A/B Schedule
ADSS A/B Schedule as per NRS 078-1
Item | Subclause | Description |  | Schedule A | Schedule B
B.1 | 4.1 | Number of fibres |  | 48 & or 24 cores
B.2 | 4.1 | Type of fibre |  | As in NRS 081
B.3 | 4.2.2 | Mass per length of cable | kg/km | < 200
B.4 | 4.2.2 | Cable diameter | mm | ≤ 15
B.5 | 4.2.2 | Maximum bending radius |  | 250 mm
B.6 | 4.2.6 | Cabled cut-off wavelength | nm | ≤ 1 260 nm
B.7 | 4.2.7 | Details of measures taken and tests performed for UV |  | XXXXXXXXXX
| 4.2.8 | Cable markings on outer layer |  | None
| 8.1.2 | Cable markings on bedding layer |  | Yes
B.8 | 4.2.8 | Anti-tracking sheath |  | Yes
B.9 | 4.2.8 | Sheath tracking performance (maximum permitted leakage current under heavy pollution conditions, 100 kΩ/m longitudinal resistance). As given in IEEE 1222 | mA | XXXXXXXXXX
B.10 | 4.2.9 | Details of measures against water penetration |  | XXXXXXXXXX
B.11 | 4.2.10 | Details to minimize fibre hydrogen absorption |  | XXXXXXXXXX
B.12 | 4.2.11 | Maximum design span length | m | 400 (or as otherwise agreed)
B.13 | 4.2.11 | Ultimate tensile strength (UTS) | kN | ≥ 35,0 (or as specified for specific application)
B.14 | 4.2.11 | Maximum working load (where fibre strain does not exceed 0,2 % in the fibres) (MAT) | kN | XXXXXXXXXX
B.15 | 4.2.11 | Maximum continuous load (fibre under no strain) (MOT) | kN | XXXXXXXXXX
B.16 | 4.2.18 | Long-term creep |  | XXXXXXXXXX
B.17 | 5 | Compliance with environmental requirements |  | Yes
B.18 | 6.2.1 | Type test reports available. |  | Comply
B.19 | 6.2.12 | Details of electrical design tests performed to prove withstand capability of cable |  | XXXXXXXXXX
B.20 | 8.2.1 | Wound length | m | XXXXXXXXXX
B.21 | 9.1 | All documentation as listed in 9.1 to be supplied |  | Comply

## ADSS Table A3.2
Table A3.2 Mandatory Criteria ADSS Type Tests Required
Type Tests (Yes/No/FAT) Indicate which Tests have been submitted and which will be available at FAT NOTE: 80% test for each cable must be submitted |  |  | 48 core | Yes
No
FAT
1 | UV resistance | IEC 60794-1-22
2 | Electrical withstand capability of the sheath (tracking test) | SANS 62217:2013
3 | Water Penetration | BS EN/IEC 60794-1-22:2018
4 | Tensile Strength | BS EN/IEC 60794-1-21
5 | Crush Resistance | BS EN/IEC 60794-1-21
6 | Cable Bending | BS EN/IEC 60794-1-21
7 | Cable Torsion | BS EN/IEC 60794-1-21
8 | Impact Resistance | BS EN/IEC 60794-4-20
9 | Aeolian Vibration | BS EN/IEC 60794-1-21
10 | Galloping | BS EN/IEC 60794-1-21
11 | Creep | IEC 61395
12 | Temperature Cycling | BS EN/IEC 60794-1-22:2018
13 | Compound Flow (drip) | BS EN/IEC 60794-1-21
14 | Bending under test | BS EN/IEC 60794-1-21
15 | Hardware fitting compatibility test | BS EN/IEC 60794-4
Note: Drop down boxes for ease of use.
Please indicate YES, NO or FAT for status of Type Tests

## ADSS Table A3.3
Table A3.3 Mandatory Criteria Provide an Indexed File with answers to the following statements
Item # | Manufacturing Methods/Product Conformance | State location in File (eg. Tab 1, Tab 2, Tab A, Tab B)
1 | Factory Information: • Manufacturing premises address, • Staff organogram, • Equipment, • Testing facilities and • Plant layout
2 | Ability to provide verification of all material utilised in the production of ADSS cable • fibre cores, • Dielectric sheath, • tube, • kevlar and • gel (or similar)
3 | Ability to produce complete fibre product- ADSS • manufacture of fibre tube • drawing of fibre cores into tube • addition of gel with fibre cores • setting up of machine with dielectric material and fibre tube • assemblying of complete product (or similar process)
4 | Manufacturing to standards, licenses etc. IEC, Eskom spec etc. • Specs available on premises • Staff knowledge on specs • Implementation of specs
5 | Design Capabilities of supplier- In house or external experts etc. • Personnel and • Software
6 | Affiliations with any international organisation/ experts in the field.
7 | History and list of external customers that you have supplied similar products to.
8 | Type of testing facilities. • Calibration of equipment (major equipment calibrated accordingly), • Test capabilities (able to perform in-house sample/production tests - Test report and generic testing forms to be submitted), • Competencies of Technicians (ability to perform in-house tests), • Quality of Test reports (all relevant testing infomation available on test report)
9 | Confirmation of Type Testing Procedures (2pt) and Facilities (2pt) (confirm that supplier has ability to type test products in accordance to IEC/BS 60794-1-21, IEC 60794-1-20, Iec 60794-4, SANS 60793-1-44, 60794-1-22, IEC 61089 and IEC 61395)
10 | Can provide typical packaging details of items after manufacture. • Treatment of packaging (drums), • Drum design
11 | Marking on drums as per Eskom requirements (NRS 078-1)
12 | Handling and storage requirements of product as per manufacturer.
13 | Verification of product length on drum
14 | Verification of drum gross and net weight.

## ADSS Cable DeskScoring Criteria (hidden)
Desktop Evaluation
ADSS Cable Scoring Criteria | Maximum Score | Threshold | Actual Score | Comments
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) | 51 | 80%/33.6 | 0
ADSS Cable Scoring Criteria | Maximum Score | Threshold | Actual Score | Comments
Factory Information - File scored on answers to Table#3 on Factory information | 39 | 80%/31.2 | 0
Threshold 85% | 39 |  | 0
33.15

## InputScoring Sheet
|  |  | OEM x |  | Criteria | Score | Yes
| Threshold |  | 10kA |  | Fully compliant | 3 | No
Type Tests | 80% /36pts |  | 0 |  | Partially compliant (minor deviation) | 1
Data Sheets | 100% |  | 0 |  | Non-compliant (major deviation) | 0
ADSS information for PLSCADD. Co-efficients/ sag and tension data. | 100% |  | 0
| Total |  | 0
| Type Tests Required |  | Test Reference | Tender’s Response (Yes/No/FAT)
1 | UV resistance |  | IEC 60794-1-22
2 | Electrical withstand capability of the sheath (tracking test) |  | SANS 62217:2013
3 | Water Penetration |  | BS EN/IEC 60794-1-22:2018
4 | Tensile Strength |  | BS EN/IEC 60794-1-21
5 | Crush Resistance |  | BS EN/IEC 60794-1-21
6 | Cable Bending |  | BS EN/IEC 60794-1-21
7 | Cable Torsion |  | BS EN/IEC 60794-1-21
8 | Impact Resistance |  | BS EN/IEC 60794-4-20
9 | Aeolian Vibration |  | BS EN/IEC 60794-1-21
10 | Galloping |  | BS EN/IEC 60794-1-21
11 | Creep |  | IEC 61395
12 | Temperature Cycling |  | BS EN/IEC 60794-1-22:2018
13 | Compound Flow (drip) |  | BS EN/IEC 60794-1-21
14 | Bending under test |  | BS EN/IEC 60794-1-21
15 | Hardware fitting compatibility test |  | BS EN/IEC 60794-4
|  |  | Total | 0
|  |  | Threshold 80% | 36
Data Sheets | Manufacturer Specification
PLSCADD Info | Co-efficents, Sag & Tension Data
Type Tests | Fully Compliant | 3 : Yes & FAT | Type Test is completely correct against the relevant testing criteria
| Non-Compliant | 0: No | Type test pages missing, Type Test has failed, No type test submitted
Data Sheets | Fully Compliant | 3 : Yes & FAT | Complete data sheet with unique number identification and all relevant information
| Non-Compliant | 0: No | No data sheet or incorrect data sheet
PLSCADD Info | Fully Compliant | 3 : Yes & FAT | Completely supplied
| Non-Compliant | 0: No | Not supplied

## FAT site scoring
Factory Scoring Desktop & Factory Site
Item # | Manufacturing Methods/Product Conformance | Max Score | Actual Score Desktop | Actual Score Factory
1 | Factory Information: • Manufacturing premises address, • Staff organogram, • Equipment, • Testing facilities and • Plant layout | 5
2 | Ability to provide verification of all material utilised in the production of ADSS cable • fibre cores, • Dielectric sheath, • tube, • kevlar and • gel (or similar) | 5
3 | Ability to produce complete fibre product- ADSS • manufacture of fibre tube • drawing of fibre cores into tube • addition of gel with fibre cores • setting up of machine with dielectric material and fibre tube • assemblying of complete product (or similar process) | 5
4 | Manufacturing to standards, licenses etc. IEC, Eskom spec etc. • Specs available on premises • Staff knowledge on specs • Implementation of specs | 3
5 | Design Capabilities of supplier- In house or external experts etc. • Personnel and • Software | 2
6 | Affiliations with any international organisation/ experts in the field. | 1
7 | History and list of external customers that you have supplied similar products to. | 2
8 | Testing Capacity: • Calibration of equipment (major equipment calibrated accordingly), • Test capabilities (able to perform in-house sample/production tests - Test report and generic testing forms to be submitted), • Competencies of Technicians (ability to perform in-house tests), • Quality of Test reports (all relevant testing infomation available on test report) | 4
9 | Confirmation of Type Testing Procedures (2pt) and Facilities (2pt) (confirm that supplier has ability to type test products in accordance to IEC/BS 60794-1-21, IEC 60794-1-20, Iec 60794-4, SANS 60793-1-44, 60794-1-22, IEC 61089 and IEC 61395) | 4
10 | Can provide typical packaging details of items after manufacture. • Treatment of packaging (drums), • Drum design | 2
11 | Marking on drums as per Eskom requirements (NRS 078-1) | 1
12 | Handling and storage requirements of product as per manufacturer. | 2
13 | Verification of product length on drum | 1
14 | Verification of drum gross and net weight. | 2
| Total | 39 | 0 | 0
| Threshold 80% | 31.2