## Slide 1: Clarification for Fibre Optic Cables:
Presented by: Tshepiso Moloisane / Lesiba Buthane
Date: 28 November 2025

## Slide 2: OPGW: 2009DXGP

## Slide 3: Scope - OPGW
Technical Tender Evaluation Procedure
Optical Ground Wire (OPGW) cables technical evaluation criteria is a process by which an inquiry is evaluated and scored to assess supplier’s capability to enter a supply contract with Eskom. A complete evaluation of a potential supplier would involve a desktop evaluation and factory evaluation. The factory evaluation is necessary to verify if the supplier possesses the capabilities which they have documented in their tender submissions.
Any tenderers who have been assessed by Eskom within the past 36 months for the supply of OPGW may be exempted from the technical factory evaluation. These tenderers are still required to submit all technical documents as per evaluation criteria.

## Slide 4: Technical Tender Evaluation Procedure - OPGW
To ensure comprehensive technical evaluation, all tender submissions shall consist of but not limited to:
Complete Table A3.1. : OPGW Table A3_1_OPGW List.xlsx
This is in Annex A and an excel version with drop down boxes is submitted with the tender pack. This will give an indication of which OPGW cables are offered.
Complete Table A3.2. : OPGW Table A3_2 Type Test Status.xlsx
This is in Annex B and an excel version with drop down boxes is submitted with the tender pack. This is required as to the status of the type tests for the OPGW cables offered.
Complete Table A3.3. :OPGW Table A3_3 Factory File Index.xlsx
This is in Annex C and an excel version is submitted with the tender pack. A fully indexed and comprehensive file with relevant factory information is required.
Complete Table A3.4. : OPGW Table A3_4 AB Schedules.xlsx
This is in Annex D and an excel version with various columns is submitted with the tender pack. The fully completed A/B Schedules are required for each OPGW cable offered.
The Manufacturer’s Data Sheets per OPGW cable tendered is required for desktop evaluation.
The OPGW information for PLS-CADD with the co-efficient and sag and tension data shall be included for each OPGW tendered.
It must be noted that before any OPGW fibre optic cable is used on Eskom’s system, a mechanical compatibility test shall be done with the designated hardware. Agreement between prospective fibre optic cable supplier and prospective hardware supplier shall be concluded. Eskom’s only responsibility with this aspect is to review the final test results and on occasion witness these tests.
Tenderers shall ensure that they cater for the manufacture of special cables that may be requested during the contract lifetime.

## Slide 5: Technical Tender Evaluation Procedure - OPGW
Table 2 provides a summary of all the documents that are required from the Tenderers.
Table 2: Requirements from Tenderers
Step # | Activities and Submission Summary for Tenderers
1 | Submit a properly indexed Technical File
2 | Submit completed Table A3.1 - OPGW cables offered
3 | Submit completed Table A3.2 - TYPE TESTS status
4 | Submit completed Table A3.3 - FACTORY FILE index completed
5 | Submit completed Table A3.4 - A/B Schedules per OPGW offered
6 | Submit most recent TESTS reports for every OPGW offered
7 | Submit most recent DATA SHEETS for every OPGW offered
8 | Submit most recent PLSCADD information for every OPGW offered
9 | Submit indexed file with Factory Information correlating to Table A3.3

## Slide 6: Guideline for OPGW Mechanical and Electrical Parameters
kA rating | Diameter-mm (smaller the better) Can even be less than our min value | RTS-kN | DC resistance-(Ω/km) | Weight-kg/km (smaller the better, can even be less than our min value)
5 | 10.3<11.8 | >60 | 0.87<1.08 | 394<453
10 | 13.3<14 | >60 | 0.399<0.494 | 494<584
12 | 14.9<15.9 | >60 | 0.27<0.4 | 496<697
16 | 16.6<17.7 | >60 | 0.2<0.285 | 587<745
18 | 17.7<18.4 | >60 | 0.18<0.252 | 627<841
21 | 19.3<20 | >60 | 0.159<0.211 | 1002<731
The below table provides a guide on acceptable OPGW Cable Mechanical and Electrical parameters when populating the Schedule A/B

## Slide 7: Mandatory Criteria for Evaluation: OPGW Cable
Mandatory for Evaluation requirements are assessed on a Yes/ NO basis to determine whether the requirements are met or not. A completed submission of Tables A3.1, A3.2, A3.3 and A3.4 is mandatory. A “No” or incomplete submission of any of requested item on Table A3.1 or A3.2 or A3.3 or A3.4 will disqualify the tenderer and will not proceed further to the Desktop evaluation.
Technical Evaluation Team will check all the submissions to ensure mandatory requirements are met as a start to the Desktop Evaluation
OPGW Cable Mandatory Criteria | Comply (Yes/No)
Specify which cables can be manufactured and supplied (Complete Table A3.1) | 
State which tests are submitted and which will be provided during Factory Evaluation. (Complete Table A3.2) | 
File of information supplied for Factory Evaluation (Complete Table A3.3) | 
A and B Schedules completed to Eskom requirements for the OPGW cables provided in English from the latest NRS 061-1 (Complete Table A3.4) | 
Threshold | 100% (All “Yes”)

## Slide 8: 3.2 Desktop Evaluation : OPGW Cable
Submissions that pass the Mandatory criteria will proceed to the Desktop Evaluation.
The desktop assessment will score the following items:
OPGW test reports – only OPGW cables that were submitted as part of the tender shall be evaluated.
Manufacturer’s Data Sheets per OPGW cable that was submitted for tender.
The PLS-CADD information with the co-efficient and sag & tension data for each OPGW submitted for tender shall be included.
The items will be scored as per the Table below:
Criteria | Score
Fully compliant | 3
Non-compliant (major deviation) | 0

## Slide 9: 3.2 Desktop Evaluation : OPGW Cable
Each Tenderer will be scored per kA rating of the OPGW submitted as indicated in Table below.
OPGW cable score that passes ALL pre-set threshold in Table below shall be considered for the tender.
OPGW Cable Scoring Criteria | Maximum Score | Threshold
Each offered OPGW Cable Tests (10kA, 12kA, 16kA, 18kA, 21kA) | 36 | 80% / 28.8
Data Sheets Submitted per cable Offering | 3 | 100% / 3
PLSCADD (Co-efficient/ sag and tension data) information per Cable offering | 3 | 100% / 3

## Slide 10: Desktop Factory File Assessment : OPGW Cable
The Factory Information File shall be scored as per below Table. A score of 1 point is given for every item requested and is required to pass the threshold score (33.6/80%).
OPGW Cable Scoring Criteria | Maximum Score | Threshold
Factory Information - File scored on answers to Table 7 on Factory information | 42 | 80%/33.6

## Slide 11: Factory Assessment (On-site) : OPGW Cable
These assessments are performed to assess the tenderer’s capability to enter a contract with Eskom with respect to a specific product or service and meet Eskom’s requirements.
Type of tests that were indicated “FAT” in Table A3.2 (for Desktop evaluation) shall be provided during the factory visit. Other outstanding tests to be provided at contract award.

## Slide 12: Scope for Factory Assessment (On-site): OPGW Cable
Eskom will do factory assessments to assess the ability and readiness of the tenderer for supplying/manufacturing OPGW fibre optic cables.
Eskom assessment representative(s) will arrange visits to the factories that have met Desktop evaluation threshold.
The Eskom assessment representative(s) will conduct the assessment using Table provided in Technical Evaluation Criteria.
The requirements in the Desktop evaluation will be verified. If a tenderer scores less than the threshold of 80%, they will be disqualified.
The OEM’s local representative shall be available on site at the manufacturing premises during the virtual or during the factory assessment and will be required to present during the assessment.

## Slide 13: Questions?

## Slide 14: ADSS : E2037DXGP

## Slide 15: Summary of Documents related to the technical evaluation
The technical evaluation procedure is specific to the ADSS cable specifications. The complete evaluation of any potential supplier would involve a desktop evaluation as well as a factory evaluation. The factory evaluation is necessary to verify the capabilities which the supplier would have documented in their tender submissions.
Any tenderers who have been assessed by Eskom within the past 36 months for the supply of ADSS may be exempted from the technical factory evaluation. These tenderers are still required to submit all technical documents as per evaluation criteria.
The assessment team has no authority or responsibility in the decision taken by Eskom with respect to contracting for a product or service.

## Slide 16: Technical Tender Evaluation Procedure - ADSS
To ensure comprehensive technical evaluation, all tender submissions shall consist of but not limited to:
Complete Table A3.1.:ADSS Cables _Table A3.1_ schedule A&B.xlsx
This is in Annex A and an excel version with various columns is submitted with the tender pack. The fully completed A/B Schedules are required for the ADSS cable offered.
Complete Table A3.2. :ADSS Cables_TableA3.2_Mandatory Cable Tests.xlsx
This is in Annex B and an excel version with drop down boxes is submitted with the tender pack. This is required as to the status of the type tests for the ADSS cable offered.
Complete Table A3.3. : ADSS Cables Table A3.3_Indexed Factory File.xlsx
This is in Annex C and an excel version is submitted with the tender pack. A fully indexed and comprehensive file with relevant factory information is required.
The Manufacturer’s Data Sheets for the ADSS cable tendered is required for desktop evaluation.
The ADSS information for PLS-CADD with the co-efficient and sag and tension data shall be included for the ADSS cable tendered.
It must be noted that before any ADSS fibre optic cable is used on Eskom’s system, a mechanical compatibility test shall be done with the designated hardware. Agreement between prospective fibre optic cable supplier and prospective hardware supplier shall be concluded. Eskom’s only responsibility with this aspect is to review the final test results and on occasion witness these tests.
Tenderers shall ensure that they cater for the manufacture of special ADSS cables that may be requested during the contract lifetime.

## Slide 17: Technical Tender Evaluation Procedure : ADSS Cable
Table 2 provides a summary of all the documents that are required from the Tenderers.
Table 2: Requirements from Tenderers
Steps # | Activities for Eskom Technical Assessment Team
1 | Find Tables A3.0, A3.1, A3.2, A3.3
2 | Complete Table 3.0 Mandatory Criteria
3 | Proceed to evaluate Tenderer that meets Table 3.0 Mandatory Criteria
4 | Evaluate Technical File of Tenderer
5 | Review submission for Table A3.1 and score Table A3.2 for the submitted ADSS - link with Type Test report submitted
6 | Review Indexed Factory File submission and score Table 6
7 | Review Data Sheets information submitted for the ADSS and score
8 | Review PLSCADD information submitted for the ADSS and score
9 | Consolidate Scores for Desktop evaluation from steps 6, 7 and 8 above
10 | Feedback draft report to Commercial indicating which Tenderers have passed Desktop evaluation
11 | Commercial to inform tenderer and indicate dates for Factory visits (where applicable)
12 | Factory Visits by Cross-functional team (where applicable)
13 | Final Report completed

## Slide 18: Mandatory Criteria for Evaluation : ADSS
The Eskom evaluating representatives will go through the details of the technical returnable submissions that are required to ensure that the Mandatory criteria are met. Tender submissions for Tables A3.1, A3.2 and A3.3 will be checked for existence and completeness. Submissions that receive a “No” on any of the Mandatory criteria will not be able to proceed to the Desktop Evaluation and will immediately fail the technical evaluation.
Technical Evaluation Team will check all the submissions to ensure mandatory requirements are met as a start to the Desktop Evaluation
ADSS Cable Mandatory Criteria | Mandatory | Comply (Yes/No)
A and B Schedules completed to Eskom requirements for the ADSS cables provided in English As per NRS 078-1 format? (Complete Table A3.1) | Yes | 
State which Type tests are submitted and which will be provided during Factory Evaluation. (Complete Table A3.2) | Yes | 
File of information supplied for Table A3.3 for Factory Evaluation | Yes | 

## Slide 19: 3.2 Desktop Evaluation: ADSS Cable
Submissions that pass the Mandatory criteria will proceed to the Desktop Evaluation.
The desktop assessment will score the following items:
ADSS Type tests reports – only ADSS cables that were submitted as part of the tender shall be evaluated according to Table A3.2.
Manufacturer’s Data Sheets per ADSS cable that was submitted for tender.
The PLS-CADD information with the co-efficient and sag & tension data for each ADSS submitted for tender shall be included.
Each Tenderer will be scored for the ADSS cable submitted as indicated below:
The ADSS cable score that passes the threshold score (40.8/80%) shall be considered for the tender.
Criteria | Score
Fully compliant | 3
Partially compliant (minor deviation) | 1
Non-compliant (major deviation) | 0
ADSS Cable Scoring Criteria | Maximum Score | Threshold
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) | 45 | 80%/36
Data Sheets | 3 | None
ADSS information for PLSCADD. Co-efficient, sag and tension data. | 3 | None
Total | 51 | 80%/40.8

## Slide 20: Desktop Factory File Assessment : ADSS Cable
The Factory Information File shall be scored as per Table 6. A score of 1 point is given for every item requested. The detailed scoring in Table 7 Scoring of items in Factory Evaluation (in section 3.3.1) will be used in the Desktop and Factory site evaluations.
The Factory information file will also be scored for Desktop evaluation and is required to pass the threshold score (31.2/80%).
ADSS Cable Scoring Criteria | Maximum Score | Threshold
Factory Information - File scored on answers to Table#7 on Factory information | 39 | 80%/31.2

## Slide 21: Factory Assessment (On-site) : ADSS Cable
These assessments are performed to assess the tenderer’s capability to enter a contract with Eskom with respect to a specific product or service and meet Eskom’s requirements.
Type of tests that were indicated “FAT” in Table A3.2 (for Desktop evaluation) shall be provided during the factory visit. Other outstanding tests to be provided at contract award.

## Slide 22: Scope for Factory Assessment (On-site) : ADSS Cable
Eskom will do factory assessments to assess the ability and readiness of the tenderer for supplying/manufacturing ADSS fibre optic cable.
Eskom assessment representative(s) will arrange visits to the factories for the tenderers that have met Desktop evaluation threshold.
The Eskom assessment representative(s) will conduct the assessment using Table provided in Technical Evaluation Criteria.
The requirements in the Desktop evaluation will be verified. If a tenderer scores less than the threshold of 80%, they will be disqualified.
The OEM’s local representative shall be available on site at the manufacturing premises during the virtual or during the factory assessment and will be required to present during the assessment.

## Slide 23: DUCT FIBRE OPTIC CABLES: E2038DXGP

## Slide 24: Scope - DUCT FIBRE OPTIC CABLES
Technical Tender Evaluation Procedure
The technical evaluation procedure is specific to the DUCT fibre optic cable specifications. The complete evaluation of any potential supplier would involve a desktop evaluation as well as a factory assessment. The factory evaluation is necessary to verify if the supplier possesses the capabilities which they have documented in their tender submissions.

## Slide 25: Technical Tender Evaluation Procedure
During Tender evaluation, the evaluation team will follow these steps in evaluating submissions from the Tenderer :
Annexes Hyperlink: DUCT Cables Scoring Rev2.xlsx
Steps # | Activities for Eskom Technical Evaluation Team
1 | Letter stating the minimum drums length that can be supplied (Minimum drum length for the Multimode Fibre is 500m. The Minimum drum length for the Single mode fibre is 3000m)
2 | Confirm tenderer provided complete Tables A2.1, A2.2, A2.3, A2.4, A2.5
3 | Confirm tenderer provided Table 2 Mandatory Criteria requirements
4 | Proceed to evaluate Tenderer that meets Table 2 Mandatory Criteria
5 | Conduct Desktop evaluation using Technical File of Tenderer
6 | Review submission for Tables A2.3 and A2.4 and score using Table 5 for the submitted DUCT Cable
7 | Review Data Sheets information submitted for the DUCT and score using Table 5.
8 | Review Indexed Factory File submission and score using Table 6.
9 | Consolidate Scores for Desktop evaluation from steps 6, 7 and 8 above.
10 | Commercial to inform tenderer and indicate dates for Factory visits (where applicable)
11 | Factory Visits by Cross-functional team (where applicable)
12 | Feedback draft report to Commercial indicating which Tenderers have passed Desktop evaluation threshold.
13 | Final Report completed

## Slide 26: Desktop Evaluation: Mandatory Criteria Evaluation
This evaluation exercise is performed by the Eskom evaluating representatives. The Eskom evaluating representatives will go through the details of the returnable submissions that are required and will ensure that the Mandatory criteria are met. Submissions that receive a “No” on any of the Mandatory criteria will not be able to proceed to the Desktop Evaluation and therefore will immediately fail the technical evaluation.
DUCT Cable Mandatory Criteria | Mandatory | Comply (Yes/No)
Letter stating the minimum drums length can be supplied (Minimum drum length for the Multimode Fibre is 500m. The Minimum drum length for the Single mode fibre is 3000m) | Yes | 
A/B Schedules for Single mode DUCT cables provided in English (Complete Table A2.1) | Yes | 
A/B Schedules Multimode DUCT cables provided in English (Complete Table A2.2) | Yes | 
State which Single Mode Cable tests are submitted, and which will be provided during Factory Evaluation. (Complete Table A2.3) | Yes | 
State which Multimode Cable tests are submitted, and which will be provided during Factory Evaluation. (Complete Table A2.4) | Yes | 
File of information supplied for Table A2.5 for Factory Evaluation | Yes | 

## Slide 27: Desktop Evaluation: Qualitative Assessment
All Tender submissions that passes the Mandatory criteria will proceed to the full Desktop Qualitative Evaluation.
The desktop assessment will score the following items:
  DUCT cable tests reports – Both Single mode and multimode DUCT cables are required.
  Manufacturer’s Data Sheets per DUCT cable that was submitted for tender.
Items submitted will be scored as follows:
Criteria | Score
Fully compliant | 3
Non-compliant (major deviation) | 0

## Slide 28: Desktop Evaluation: Qualitative Assessment..Cn’t
Each Tenderer will be scored for the DUCT cable submitted as follows:
Note: Each cable offered will be assessed independently against the above stated threshold and cables score that passes the threshold score shall be considered for the tender.
DUCT Cable Scoring Criteria | Maximum Score | Threshold
24/48 Core Single Mode Duct Cable Test Report Scores | 24 | 80% / 19.2
12 Core Single Mode Duct Cable Test Report Scores | 24 | 80% / 19.2
Multimode 12 Core Test Report Scores | 12 | 80% / 9.6
Cable(s) on offer datasheets submissions | 3 | 100% / 3

## Slide 29: Desktop Evaluation: Desktop Factory File Assessment
The Factory Information File shall be scored as per Table 5. A score of 1 point is given for every item requested. The detailed scoring in Table 6 (in section 3.3.1) will be used in the Desktop and Factory site evaluations.
Note: The Factory information file will also be scored for Desktop evaluation and is required to pass the threshold score.
DUCT Cable Scoring Criteria | Maximum Score | Threshold 80%
Factory Information - File scored on answers to Table 6 on Factory information | 37 | 29.6

## Slide 30: Factory Assessment: Scope
These assessments are performed to evaluate the tenderer’s capability to enter a contract with Eskom with respect to a specific product or service and meet Eskom’s requirements. Type tests that were indicated “FAT” in Table A2.3 and Tables A2.4 (for Desktop evaluation) shall be provided during the factory visit.
Eskom will conduct factory assessments to assess the ability and readiness of the tenderer to supply/manufacture fibre optic cables and/or hardware for Eskom should the need arise.
Eskom assessment representative(s) will arrange visits to the factories that have qualified for factory evaluations.
The Eskom evaluation representative(s) will conduct the assessment using the Table provided in the Evaluation Criteria.
The requirements in the Desktop evaluation will be verified. If a tenderer scores less than the threshold of 80%, they will be disqualified

## Slide 31: Questions?