## DUCT Activites Tables
Steps # | Activities for Eskom Technical Assessment Team
1 | Find Letter stating minimum 500m drumsfor Multimode Fibre or 3000 For single Mode provided
2 | Find Tables A2.1, A2.2, A2.3, A2.4, A2.5
3 | Complete Table 3 Mandatory Criteria
4 | Proceed to evaluate Tenderer that meets Table 3 Mandatory Criteria
5 | Evaluate Technical File of Tenderer
6 | Review submission for Tables A2.3 and A2.4 and score Table 5 for the submitted DUCT Cable - link with Type Test report submitted
7 | Review Indexed Factory File submission and score Table 6
8 | Review Data Sheets information submitted for the DUCT and score
9 | Consolidate Scores for Desktop evaluation from steps 6, 7 and 8 above
10 | Feedback draft report to Commercial indicating which Tenderers have passed Desktop evaluation
11 | Commercial to inform tenderer and indicate dates for Factory visits
12 | Factory Visits by Cross-functional team
13 | Final Report completed
Step # | Activities and Submission Summary for Tenderers
1 | Submit a properly indexed Technical File
2 | Submit completed Tables 2.1 and Table A2.2 - A/B Schedules for DUCT cables offered
3 | Submit completed Tables A2.3 and A2.4 - TYPE TESTS status
4 | Submit completed Table A2.3 - FACTORY FILE index completed
5 | Submit most recent TYPE TESTS for the DUCT Cable offered
6 | Submit most recent DATA SHEETS for the DUCT Cable offered
7 | Submit indexed file with Factory Information correlating to Table A2.5

## DUCT Mandatory Criteria
DUCT Cable Mandatory Criteria | Comply (Yes/No)
Letter stating the minimum drums length can be supplied (Minimum drum length for the Multimode Fibre is 500m. The Minimum drum length for the Single mode fibre is 3000m)
A/B Schedules for Single mode DUCT cables provided in English (Complete Table A3.1)
A/B Schedules Multimode DUCT cables provided in English (Complete Table A2.2)
State which Single Mode Cable Type tests are submitted and which will be provided during Factory Evaluation. . (Complete Table A2.3)
State which Multimode Cable Type tests are submitted and which will be provided during Factory Evaluation. (Complete Table A2.4)
File of information supplied for Table A2.5 for Factory Evaluation
Table A2.1 Mandatory Criteria | A/B Schedule Single Mode
Table A2.2 Mandatory Criteria | A/B Schedule Multimode
Table A2.2 Mandatory Criteria | List of Type Tests Multimode
Table A2.4 Mandatory Criteria | List of items for FAT

## DUCT Table A2.1
Table A2.1 Mandatory Criteria - A/B Schedule
Single Mode DUCT A/B Schedule as per NRS 088-1 | [5 empty] | 48/24 Core Single Sheath | 12 Core Double Sheath Rodent Resistant
Item | Subclause | Description |  | Schedule A | Schedule B | Schedule B | Schedule B
1 | 4.1.1 | Number of fibres cores |  | 48,24, 12
2 | 4.1.1 | Type of fibre |  | As per NRS 081
3 | 4.2.2 | Armouring required |  | No
4 | 4.2.2 | Type of armouring |  | N/A
5 | 4.2.2 | Single-sheath or Double-sheath |  | Single sheath (48/24core) & Double-sheath(12 core)
6 | 4.2.2. | Glass Composite layer |  | Single sheath - No & Double-sheath - Yes
7 | 4.2.5 | Details of fibre colour coding |  | As in EIA/TIA 598-C
8 | 4.2.6 | Measures taken to prevent water ingress |  | Specify
9 | 4.2.7 | Toxicity and dermatological safety |  | Yes
10 | 4.2.9 | Cable tension for 0.2% fibre strain | N | Specify
11 | 4.2.11 | Crush resistance for either single or double sheath cable | N | Specify
12 | 4.2.12 | Bending radius of either single or double sheath cable |  | Specify
13 | 4.2.12 | Outer diameter of the cable |  | Specify
14 | 5.2.1 | Availability of type test reports. |  | Comply
15 | 6.2.1 | Wound length of cables on drum | m | Specify
16 | 6.2.1 | Treated wooden drum required | Yes/No | XXXXXXX
17 | 6.2.6 | Storage requirements |  | Specify
18 | 6.2.7 | Steel drum disposal |  | Specify
19 | 7.1 (a) | Manufacturer data sheet number |  | Specify
20 | 7.2 | Compliance to submissions requested in 7.2 |  | Comply
21 | 7.5 (d) | Cable mass per unit length | kg/km | Specify
22 | 7.6(b) | Effective group index of refraction at 1310 nm at 1550 nm |  | Specify

## DUCT Table A2.2
Table A2.2 Mandatory Criteria - A/B Schedule
Multi Mode DUCT A/B Schedule as per Eskom 240-72274830
Description | Schedule A Particulars of Eskom's Requirements | Schedule B Guaranteed Technical Particulars Offered
No. of Fibres | 12
Type of Fibres | OM2/OM3
Core diameter | 50µm ±6%
Cladding diameter | 125 m ±1.0mm
Core/Cladding concentricity error | Specify
Cladding non-circularity | Specify
Core non-circularity | Specify
Cladding Configuration (depressed / matched / other) | Specify
Numerical aperture | 0.2250 ± 0.02
Attenuation Coefficient
at 850 nm | <2.5 dB/km
at 1310 nm | <0.8 dB/km
Normalised Modal Distortion Bandwidth
at 850 nm | >400 MHz.km
at 1310 nm | >630 MHz.km
Proof Test | 1% elongation
Cable Diameter (mm) | Specify
Weight of Cable (kg/km) | Specify
Ultimate Tensile Strength (kN) | Specify
Maximum Short Term Load(Maximum strain less than 33 % fibre proof strain level) (kN) | Specify
Test Load(where fiber strain does not exceed 0.2% in the fibres) (kN) | Specify
Maximum continuous load(fiber under no strain) (kN) | Specify
Minimum Bending Radius (mm) | 150 mm
Metal free cable
Crush Resistance | 1000N
Metal free cable
Impact Resistance | 1 x 50 Nm
Metal free cable
Rodent Resistant | Yes
HDD with double polyethylene sheath and glass yarn/composite layer | Yes
Maximum Cable Length available per drum | Specify
Metal free cable

## DUCT Table A2.3
Table A2.3 Mandatory Criteria Single Mode Type of Tests Required as per NRS 088-1
Type Tests (Yes/No/FAT) Indicate which Tests have been submitted and which will be available at FAT |  |  |  | YES
|  | 48/24 Core Single Sheath | 12 Core Double Sheath | NO
1 | Longitudinal Water Penetration (SANS 60794-1-2) |  |  | FAT
2 | Sheath UV withstand (ISO 4892-3)
3 | Tensile Strength (SANS 60794-1-2)
4 | Crush Resistance (SANS 60794-1-2)
5 | Cable Bending (SANS 60794-1-2)
6 | Cable Twist (SANS 60794-1-2)
7 | Impact Resistance (SANS 60794-1-2)
8 | Temperature Cycling (SANS 60794-1-2)
9 | Compound Flow (drip) (SANS 60794-1-2)
10 | Sheave Test (SANS 60794-1-2)

## DUCT Table A2.4
Table A2.4 Mandatory Criteria Multimode Type of Tests Required as per 240-72274830
Type Tests (Yes/No/FAT) Indicate which Tests have been submitted and which will be available at FAT |  | YES
3 | Tensile Strength (60794-1-E1) | NO
4 | Crush Resistance (60794-1-E3) | FAT
7 | Impact Resistance (60794-1-E4)
8 | Temperature Cycling (IEC 60794-1-2-F1.)

## DUCT Table A2.5
Factory Scoring Desktop & Factory Site
Item # | Manufacturing Methods/Product Conformance | Max Score | Actual Score Desktop | Actual Score Factory
1 | Factory Information: | 5
· Manufacturing premises address
· Staff organogram
· Equipment,
· Testing facilities and• Plant layout
2 | Ability to provide verification of all material utilised in the production of ADSS cable | 5
• fibre cores,
· Dielectric sheath,
· tube,
· kevlar and
· gel
· rodent resistant
(or similar)
3 | Ability to produce complete fibre product- ADSS | 5
manufacture of fibre tube
· drawing of fibre cores into tube
· addition of gel with fibre cores
· setting up of machine with dielectric material and fibre tube
· assemblying of complete product
(or similar process)
4 | Manufacturing to standards, licenses etc. IEC, Eskom spec etc. | 3
· Specs available on premises
· Staff knowledge on specs
· Implementation of specs
5 | Design Capabilities of supplier- In house or external experts etc. | 2
· Personnel and
· Software
6 | Affiliations with any international organisation/ experts in the field. | 1
7 | History and list of external customers that you have supplied similar products to. | 2
8 | · Type of testing facilities. | 4
Calibration of equipment (major equipment calibrated accordingly),
· Test capabilities (able to perform in-house sample/production tests - Test report and generic testing forms to be submitted),
· Competencies of Technicians (ability to perform in-house tests),
· Quality of Test reports (all relevant testing infomation available on test report)
9 | Confirmation of Type Testing Procedures (2pt) and Facilities (2pt) (confirm that supplier has ability to type test products in accordance to SANS/IEC 60794-1-2, ISO 4892-3. | 4
10 | Can provide typical packaging details of items after manufacture. | 2
• Treatment of packaging (drums), • Drum design
11 | Marking on drums as per Eskom requirements (NRS 088-1) | 1
12 | Handling and storage requirements of product as per manufacturer. | 1
13 | Verification of product length on drum | 1
14 | Verification of drum gross and net weight. | 1
| Total | 37 | 0 | 0
| Threshold 80% | 29.6

## DUCT FAT Scoring
Factory Scoring Desktop & Factory Site
Item # | Manufacturing Methods/Product Conformance | Max Score | Actual Score Desktop | Actual Score Factory
1 | Factory Information: • Manufacturing premises address, • Staff organogram, • Equipment, • Testing facilities and • Plant layout | 5
2 | Ability to provide verification of all material utilised in the production of DUCTS cable • fibre cores, • Dielectric sheath, • tube, • water blocking and • gel • rodent resistant (or similar) | 5
3 | Ability to produce complete fibre product- DUCT • manufacture of fibre tube • drawing of fibre cores into tube • addition of gel with fibre cores • setting up of machine with dielectric material and fibre tube • assemblying of complete product (or similar process) | 5
4 | Manufacturing to standards, licenses etc. IEC, Eskom spec etc. • Specs available on premises • Staff knowledge on specs • Implementation of specs | 3
5 | Design Capabilities of supplier- In house or external experts etc. • Personnel and • Software | 2
6 | Affiliations with any international organisation/ experts in the field. | 1
7 | History and list of external customers that you have supplied similar products to. | 2
8 | Type of testing facilities. • Calibration of equipment (major equipment calibrated accordingly), • Test capabilities (able to perform in-house sample/production tests - Test report and generic testing forms to be submitted), • Competencies of Technicians (ability to perform in-house tests), • Quality of Test reports (all relevant testing infomation available on test report) | 4
9 | Confirmation of Type Testing Procedures (2pt) and Facilities (2pt) (confirm that supplier has ability to type test products in accordance to SANS/IEC 60794-1-2, ISO 4892-3, | 4
10 | Can provide typical packaging details of items after manufacture. • Treatment of packaging (drums), • Drum design | 2
11 | Marking on drums as per Eskom requirements (NRS 088-1) | 1
12 | Handling and storage requirements of product as per manufacturer. | 1
13 | Verification of product length on drum | 1
14 | Verification of drum gross and net weight. | 1
| Total | 37 | 0 | 0
| Threshold 80% | 29.6 | 0 | 0

## InputScoring Sheet
|  | OEM x |  |  | Criteria | Score | Yes
| Threshold | Single Mode DUCT 24/48 core | Single Mode DUCT 12 core | Multimode DUCT 12 Core | Fully compliant | 3 | No
Type of Tests | 80% Per Cable Catergory | 0 | 0 | 0 | Partially compliant (minor deviation) | 1
Data Sheets | 100% | 0 | 0 | 0 | Non-compliant (major deviation) | 0
| Total | 0 | 0 | 0
|  | Single Mode DUCT 24/48 core single sheath | Single Mode DUCT 12 core double sheath | Multimode DUCT
| Type Tests Required | Score 3 or 0 below
1 | Longitudinal Water Penetration (SANS 60794-1-2)
2 | Sheath UV withstand (ISO 4892-3)
3 | Tensile Strength (SANS 60794-1-2)
4 | Crush Resistance (SANS 60794-1-2)
5 | Cable Bending (SANS 60794-1-2)
6 | Cable Twist (SANS 60794-1-2)
7 | Impact Resistance (SANS 60794-1-2)
8 | Temperature Cycling (SANS 60794-1-2)
9 | Compound Flow (drip) (SANS 60794-1-2)
10 | Sheave Test (SANS 60794-1-2)
| Total Score | 0 | 0 | 0
| Threshhold @80% | 24 | 24 | 9.6
Data Sheets | Manufacturer Specification
Type Tests | Fully Compliant | Type Test is completely correct against the relevant testing criteria
| Non-Compliant | Type Test has failed, No type test submitted
Data Sheets | Fully Compliant | Complete data sheet with unique number identification and all relevant information
| Non-Compliant | No data sheet or incorrect data sheet

## DUCT Cable DeskScoring Criteria
Desktop Evaluation
DUCT Cable Scoring Criteria | Maximum Score | Actual Score | Comments
Cable Score (based on Type Tests, Data Sheet info) Single mode 48/24 core single sheath | 0 | 0
Cable Score (based on Type Tests, Data Sheet info) Single mode 12 core double sheath | 0 | 0
Cable Score (based on Type Tests, Data Shee info) Multimode | 0 | 0
Total | 0 | 0
Threshold 80% | 0
DUCT Cable Scoring Criteria | Maximum Score | Actual Score | Comments
Factory Information - File scored on answers to Table#3 on Factory information | 37 | 0
Threshold 80% | 29.6