## Activites Tables
Steps # | Activities for Eskom Technical Assessment Team
1 | Find Tables A3.1, A3.2, A3.3, A3.4
2 | Complete Table 3 Mandatory Criteria
3 | Proceed to evaluate Tenderer that meets Table 3 Mandatory Criteria
4 | Evaluate Technical File of Tenderer
5 | Review submission for Table A3.1 and score Table A3.2 for each submitted OPGW - link with Type Test report submitted
6 | Review Indexed Factory File submission and score Table 6
7 | Review Data Sheets information submitted for each OPGW and score
8 | Review PLSCADD information submitted for each OPGW and score
9 | Consolidate Scores for Desktop evaluation from steps 6, 7 and 8 above
10 | Feedback draft report to Commercial indicating which Tenderers have passed Desktop evaluation
11 | Final Report completed
Step # | Activities and Submission Summary for Tenderers
1 | Submit a properly indexed Technical File
2 | Submit completed Table A3.1 - OPGW cables offered
3 | Submit completed Table A3.2 - TYPE TESTS status
4 | Submit completed Table A3.3 - FACTORY FILE index completed
5 | Submit completed Table A3.4 - A/B Schedules per OPGW offered
6 | Submit most recent TYPE TESTS for every OPGW offered
7 | Submit most recent DATA SHEETS for every OPGW offered
8 | Submit most recent PLSCADD information for every OPGW offered
9 | Submit indexed file with Factory Information correlating to Table A3.3

## OPGW Mandatory Criteria_Table 3
OPGW Cable Mandatory Criteria | Comply (Yes/No)
Specify which cables can be manufactured and supplied (complete Table A3.1)
State which Type tests are submitted and which will be provided during Factory Evaluation. (Complete TableA3.2)
File of information supplied for Factory Evaluation (Complete Table A3.3)
A and B Schedules completed to Eskom requirements for the OPGW cables provided in English from the latest NRS 061-1 (Complete Table A3.4)
Table A3.1 Mandatory Criteria | List of OPGWs required
Table A3.2 Mandatory Criteria | List of Type Tests
Table A3.3 Mandatory Criteria | List of items for FAT
Table A3.4 Mandatory Criteria | List of A/B Schedules

## OPGW Table A3.1
Table A3.1 Mandatory Criteria Please state which OPGWs you are tendering for
kA Rating
| 10kA | 12kA | 16kA | 18kA | 21kA
Greased 48 core | [5 empty] | X
Ungreased 48 core

## OPGW Table A3.2
Table A3.2 Mandatory Criteria OPGW Type of Tests Required
Type of Tests (Yes/No/FAT) Indicate which Tests have been submitted and which will be available at FAT NOTE: 80% threshold for type tests for each cable must be submitted for Desktop Evaluation |  | Ungreased |  |  |  |  | Yes
|  | 48 core |  |  |  |  | No
|  | 10kA | 12kA | 16kA | 18kA | 21kA | FAT
1 | Crush Resistance Test (IEC 60794-1-2)
2 | Tensile Performance Test (IEC 61089)
3 | Cable deformation Test
4 | Stress-Strain Test (IEC 61089)
5 | Impact Test (IEC 60794-1-2)
6 | Sheave Test
7 | Aeolian Vibration Test
8 | Temperature Cycle
9 | Water Ingress Test (IEC 60794-1-2)
10 | Short Circuit Test (IEC 60794-1-2)
11 | Lightning Test (IEC 60794-1-2)
12 | Conductor Creep Test (IEC 61395)
Each cell has a drop down box
Please state YES, NO or FAT to indicate the status of the TYPE TEST reports.

## OPGW Table A3.3
Factory Scoring Desktop & Factory Site
Item # | Manufacturing Methods/Product Conformance | Max Score | Actual Score
1 | Factory Information – | 5
· Manufacturing premises address,
· Staff organogram,
· Equipment,
· Testing facilities and
· Plant layout
2 | Ability to provide verification of all material utilised in the production of OPGW cable | 5
· fibre cores,
· aluminium/steel strands,
· tube,
· grease and
· gel.
3 | Ability to produce complete fibre product- OPGW | 5
· Manufacture of fibre tube
· Drawing of fibre cores into tube
· Addition of gel with fibre cores
· Setting up of machine with steel/aluminium strands fibre tube
· Stranding of complete product
(or similar process)
4 | Manufacturing to standards, licenses etc. IEC, Eskom spec etc. | 3
· Specs available on premises
· Staff knowledge on specs
· Implementation of specs
5 | Design Capabilities of supplier- In house or external experts etc. | 2
· Personnel and
· Software
6 | Affiliations with any international organisation/ experts in the field. | 1
7 | History and list of external customers that you have supplied similar products. | 2
8 | Type of testing facilities. | 4
· Calibration of equipment (major equipment calibrated accordingly),
· Test capabilities (able to perform in-house sample/production tests - Test report and generic testing forms to be submitted),
· Competencies of Technicians (ability to perform in-house tests),
· Quality of Test reports (all relevant testing infomation available on test report)
9 | Confirmation of Type Testing Procedures (2pt) and Facilities (2pt) (confirm that supplier has ability to type test products in accordance to IEC 60794-1-2, IEC 61089 and IEC 61395) | 4
10 | Can provide typical packaging details of items after manufacture. | 2
· Treatment of packaging (drums),
· Drum design
11 | Packaging of drums into containers for international suppliers | 3
· container size
· layout of drums in container
· loading and off-loading requirements
12 | Marking on drums as per Eskom requirements (NRS 061-1) | 1
13 | Handling and storage requirements of product as per manufacturer. | 2
14 | Verification of product length on drum | 1
15 | Verification of drum gross and net weight. | 2
Totals |  | 42
Threshhold @ 80% |  | 33.6

## OPGW Table A3.4
Table A3.4 Mandatory Criteria Please Complete A/B Schedule as per OPGW cable tendering | [5 empty] | 10kA - Schedule B |  | 12kA - Schedule B |  | 16kA - Schedule B |  | 18kA - Schedule B |  | 21kA - Schedule B
Item | Clause | Description |  | Schedule A | Schedule B | 48 core greased | 48 core ungreased | 48 core greased | 48 core ungreased | 48 core greased | 48 core ungreased | 48 core greased | 48 core ungreased | 48 core greased | 48 core ungreased
B.1 | 4.1.4 | Grease conductor in accordance with SANS 61089? | Yes/No | Greased & Ungreased required | xxxxxxxxxx
| 4.1.5 | Pollution level, if other than heavy |  | __________ | xxxxxxxxxx
|  | Maximum temperature, if other than 50 °C | °C | __________ | xxxxxxxxxx
|  | Minimum temperature, if other than –10 °C | °C | __________ | xxxxxxxxxx
|  | Maximum wind speed, if other than 36 m/s | m/s | __________ | xxxxxxxxxx
|  | Route altitude, if other than 2 000 m | m | __________ | xxxxxxxxxx
| 4.1.6 | Name of manufacturer |  | xxxxxxxxxx | __________
|  | Place of manufacture |  | xxxxxxxxxx | __________
|  | Manufacturer’s reference number |  | xxxxxxxxxx | __________
B.2 | 4.2.1.1 | Type of fibre in accordance with NRS 081 (G.652D) | Yes/No | xxxxxxxxxx | __________
|  | If no, state fibre type |  | xxxxxxxxxx | __________
| 4.2.2.1 | OPGW 1 s current rating | kA | 10, 12, 16, 18, 21 | __________
| 4.2.2.2 | Stranding and wire diameter |  | xxxxxxxxxx | __________
B.3 | 4.3.1.1 | Number of fibres |  | 48 Core | xxxxxxxxxx
| 4.3.2.1 | Conductor material |  | xxxxxxxxxx | __________
|  | Nominal cross-section |  | xxxxxxxxxx | __________
|  | Actual cross-sectional area |  | xxxxxxxxxx | __________
|  | Maximum overall diameter |  | xxxxxxxxxx | __________
|  | Maximum mass per metre of cable-ungreased | kg/m | xxxxxxxxxx
|  | Maximum mass per metre of cable-greased | kg/m | xxxxxxxxxx | __________
|  | Rated tensile strength (RTS) |  | xxxxxxxxxx | __________
|  | Initial modulus of elasticity |  | xxxxxxxxxx | __________
|  | Final modulus of elasticity |  | xxxxxxxxx | _________
|  | Maximum drum length |  | xxxxxxxxx | _________
|  | Direction of lay of outer layer |  | xxxxxxxxxx | __________
|  | Diameter of all layer strands |  | xxxxxxxxxx | __________
|  | Short-circuit 1 s current rating |  | xxxxxxxxxx | __________
|  | Short-circuit 0.5 s current rating |  | xxxxxxxxxx
|  | DC resistance at 20 oC/km | W | xxxxxxxxxx | __________
|  | Continuous current-carrying capability | A | xxxxxxxxxx | __________
| 4.3.2.2 | Complete details of cable construction,
including measures to minimize hydrogen
|  | absorption and water ingress. |  | xxxxxxxxxx | __________
B.4 | 4.4.1 | Is a sample required? | Yes/No | No-will request if needed | xxxxxxxxxx
| 4.4.3 | Length of sample, if not 1 m |  | __________ | xxxxxxxxxx
B.5 | 5.1.3.2 | Specify class of cable 0, 1, 2 or 3 |  | 3 | xxxxxxxxxx
B.6 | 6.2.1 | Maximum drum length of OPGW |  | Xxxxxxxxxx | __________
|  | Mass of drum including max. length of OPGW cable |  | xxxxxxxxxx | __________
B.7 | 6.3 | Is documentation required? | Yes/No | Yes | xxxxxxxxxx

## OPGW Cable DeskScoring Criteria (hidden)
Desktop Evaluation
OPGW Cable Scoring Criteria | Maximum Score | Threshold | Actual Score
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) 10kA | 42 | 80%/33.6 | 42
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) 12kA | 42 | 80%/33.6 | 0
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) 16kA | 42 | 80%/33.6 | 0
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) 18kA | 42 | 80%/33.6 | 0
Cable Score (based on Type Tests, Data Sheet and PLSCADD info) 21kA | 42 | 80%/33.6 | 0

## InputScoring Sheet_
OEM x
| Maximum Score | 10kA | 12kA | 16kA | 18kA | 21kA
Type Tests | 36 | 36 | 0 | 0 | 0 | 0
Data Sheets | 3 | 3 | 0 | 0 | 0 | 0
OPGW information for PLSCADD. Co-efficients/ sag and tension data. | 3 | 3 | 0 | 0 | 0 | 0
Total | 42 | 42 | 0 | 0 | 0 | 0
Threshold 80% | 33.6
|  | 10kA | 12kA | 16kA | 18kA | 21kA
| Type Tests Required | Score 3 or 0 below
1 | Crush Resistance Test (IEC 60794-1-2) | 3
2 | Tensile Performance Test (IEC 61089) | 3
3 | Cable deformation Test | 3
4 | Stress-Strain Test (IEC 61089) | 3
5 | Impact Test (IEC 60794-1-2) | 3
6 | Sheave Test | 3
7 | Aeolian Vibration Test | 3
8 | Temperature Cycle | 3
9 | Water Ingress Test (IEC 60794-1-2) | 3
10 | Short Circuit Test (IEC 60794-1-2) | 3
11 | Lightning Test (IEC 60794-1-2) | 3
12 | Conductor Creep Test (IEC 61395) | 3
|  | 36 | 0 | 0 | 0 | 0
Data Sheets | Manufacturer Specification | 3
PLSCADD Info | Co-efficents, Sag & Tension Data | 3
Type Tests | Fully Compliant | 3 : Yes & FAT | Type Test is completely correct against the relevant testing criteria
| Non-Compliant | 0: No | Type test pages missing, Type Test has failed, No type test submitted
Data Sheets | Fully Compliant | 3 : Yes & FAT | Complete data sheet with unique number identification and all relevant information
| Non-Compliant | 0: No | No data sheet or incorrect data sheet
PLSCADD Info | Fully Compliant | 3 : Yes & FAT | Completely supplied
| Non-Compliant | 0: No | Not supplied