Part 4: Site Information

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C4 | Site Information | 1 of 9 |
|  | Total number of pages |  |

Part C4: Site Information

Annexures to C4

| Title | Annex number |
| --- | --- |
| # General description of the Site and Footprint | Annexure A |
| Scheduled Maintenance Work as priced in Price List in C2.2 | Annexure B |
| SLA Monthly Service Report Template | Annexure C |
| Contractor’s Schedule of equipment and tools | Annexure D |
| Contractor’s Organogram | Annexure E |

# Annexure A: General description of the Site and Footprint

This Site Information describes the Arnot Power Station Site and its surroundings and comprises all documents listed, together with the detailed information contained in this section. The Contractor is deemed to have inspected the Site and considered all Site conditions in planning and performing the Service.

Arnot Power Station It is situated about 220 km east of Johannesburg on the Mpumalanga Highveld along the N4 to Mbombela and Maputo. The GPS Location of Arnot Power Station is 25.94384°S 29.78956°E

The PV Site is located within the secured boundary of Arnot Power Station, located on the farm Rietkuil491 JS in the Steve Tshwete Local Municipality in Mpumalanga Province, and includes:

- The 17.2 MWac Solar Photovoltaic (PV) Plant area

- Associated equipment and infrastructure

- Access roads, perimeter fencing, drainage areas

- Safety zones, switching yards, LV/MV reticulation points

- Arnot Power Station operational facilities relevant to the Service

| GPS Location 1A (fenced area) |  |
| --- | --- |

Drawing of PV Plant

The Site falls within a controlled, high-security Eskom operational environment. All Contractor personnel require pre-authorisation, security vetting and induction.

# One-in-ten-year-return weather data obtained from SA Weather Bureau for Belfast station

If any one of these weather measurements recorded within a calendar month, before the Completion Date for the whole of the Services and at the place stated in this Contract Data is shown to be more adverse than the amount stated below then the Contractor may notify a compensation event.

BELFAST (2015-2024)

Coordinates: -25.6917, 30.0344

Altitude: 1882m

|  | One-in-ten-year-return |  |  |  |
| --- | --- | --- | --- | --- |
| Month | Cumulative rainfall (mm) | Number of days with rain more than 10mm | Number of days with min air temp < 0 °C | Number of days with snow lying at 08:00 CAT |
| January | 243 | 9 | 0 | No Data |
| February | 152 | 6 | 0 | No Data |
| March | 224.6 | 5 | 0 | No Data |
| April | 101.6 | 4 | 0 | No Data |
| May | 79.8 | 4 | 2 | No Data |
| June | 7.2 | 0 | 13 | No Data |
| July | 6.8 | 0 | 17 | No Data |
| August | 14 | 1 | 5 | No Data |
| September | 56.6 | 2 | 3 | No Data |
| October | 68.4 | 4 | 0 | No Data |
| November | 136 | 6 | 0 | No Data |
| December | 241.6 | 9 | 0 | No Data |

Only the difference between the more adverse recorded weather and the equivalent measurement given above is taken into account in assessing a compensation event.

ANNEXURE B: Planned Solar Plant Maintenance

| Solar Plant Maintenance Activities |  |  |  |
| --- | --- | --- | --- |
| No | Activity | Details | Frequency |
| 1 | Module Cleaning | Module cleaning is a straightforward but essential activity that delivers immediate and measurable improvements in energy yield. The required cleaning frequency will depend on local environmental conditions, including dust levels, rainfall patterns, and seasonal variations. At Arnot Power Station, the site typically experiences low dust levels and regular rainfall, further minimising potential soiling on the modules. Although Arnot is located inland and not in close proximity to the coast, environmental assessments indicate that the installation may still experience light airborne contaminants, including fine particulates from the coal and ash storages areas carried by prevailing winds. Overall, cleaning requirements are expected to be moderate, with cleaning performed as needed based on visual inspection, seasonal conditions, and performance monitoring data to ensure optimal plant output. | 6 Monthly |
|  |  | Module cleaning must consider environmental & human factors (like, autumn fall debris, soiling from roads & agricultural activities). |  |
|  |  | Weather patterns must be established to identify required cleaning during rainy and non-rainy periods. |  |
|  |  | Rain harvesting systems installed at the Arnot Power Station maintenance complex shall be used to provide the water requirements for the cleaning activity. The contractor shall utilise a water trailer with mobile pump accordingly where necessary. |  |
|  |  | Cleaning shall be scheduled as necessary, specifically when the PV plant efficiency falls below expectation. |  |
|  |  | Optimum frequency of cleaning can be determined by assessing the cost and benefits of conducting the procedure. The benefit of cleaning shall be seen in an improved performance ratio due to lower soiling loss and an increase in electricity generation. |  |
| 2 | Module Connection Integrity | Checking module connection integrity is important for PV systems, as faults within each string of modules may be difficult to detect. | 3 Monthly |
|  |  | Check connections between modules within each string periodically. |  |
|  |  | Measure the string current and string impedance. |  |
|  |  | String connection integrity shall additionally be monitored with the installed string level monitoring system. |  |

| Solar Plant Maintenance Activities |  |  |  |
| --- | --- | --- | --- |
| No | Activity | Details | Frequency |
| 3 | Junction / String Combiner Box | Check all Junction / String combiner boxes for water ingress, dirt & dust accumulation to prevent corrosion and or short circuits inside the boxes. | 3 Monthly |
|  |  | Check the integrity of all the connections in the boxes. Loose connections will affect the overall PV plant performance. |  |
|  |  | Check the integrity of all the Circuit Breakers and Fuses in the boxes. Loose connections will affect the overall PV plant performance. |  |
| 4 | Hot Spots | Thermography scan shall be performed across the entire PV plant to detect potential faults. | 6 Monthly |
|  |  | Thermography shall be conducted by a trained specialist using a thermographic / infrared camera. A detailed report with pictures of all string connections, junction boxes, inverters, MV infrastructure & LV infrastructure shall be compiled accordingly. |  |
|  |  | The report will identify weak and loose connections plus hot spots, which need to be corrected immediately. |  |
| 5 | Inverter Servicing | Inverter faults are the most common cause of system downtime in PV plants and shall be mitigated by stringent scheduled maintenance of inverters. | As per OEM Requirements |
|  |  | The basis of the inverter servicing requirements shall be obtained from the specific equipment manufacturer. The local operational conditions and performance of the PV plant will influence the improved inverter servicing specifications. |  |
|  |  | Minimum servicing specifications will include Visual inspections; Cleaning / Replacing of cooling fans; Removal of dust from electronic components; tightening of any loose connections; Additional analysis and diagnostics recommended by the manufacturer. |  |
| 6 | Structural Integrity | Check periodically the module mounting assembly, cable conduits & related structures for mechanical integrity and signs of corrosion. | 3 Monthly |
|  |  | Inspect support structure foundations for evidence of erosion from inter alia water run-off |  |
| 7 | Balance of Plant | Service all other PV plant auxiliary and ancillary systems which include monitoring and security systems; auxiliary power supplies; Lighting, communication systems; etcetera. | Monthly |
|  |  | Inspect and verify signal strength and continuation of connection of the communication systems within the PV plant as well as to all other external systems. |  |

| Solar Plant Maintenance Activities |  |  |  |
| --- | --- | --- | --- |
| No | Activity | Details | Frequency |
| 8 | Vegetation Control | Vegetation control and ground keeping are important scheduled tasks for the solar PV plant, as vegetation over-growth (i.e. long grass, trees or shrubs) can shade the modules - which will reduce the generation capacity of the module. Vegetation inspections and maintenance need to be conducted Monthly. | Monthly |
|  |  | Ground keeping activities need to be performed to reduce the risk of soiling onto the modules by way of leaves, pollen or dust. |  |
| 9 | General | Generate Monthly reports on system performance | Monthly |
|  |  | Periodic verification and test methodologies shall be prepared according to requirements defined in IEC 62446, IEC60364-6 and according to the current best commissioning practice. |  |
|  |  | Continual performance monitoring and error reporting of the system on a daily basis |  |
|  |  | Replacing of spare parts as and when required |  |
|  |  | Management of equipment warrantees, interfacing with equipment provider and managing logistics in replacing equipment |  |
|  |  | All equipment covered by the preventative maintenance scope is subject to corrective maintenance for wear-an-tear and breakage under normal conditions |  |

| Solar Plant Maintenance Activities |  |  |  |
| --- | --- | --- | --- |
| No | Activity | Details | Frequency |
| 10 | Unscheduled Maintenance | Unscheduled Maintenance is carried out in response to failures which shall be responded to on-site within 2 hours of when the call is logged. Where possible the fault can be rectified remotely. | Continuously |
|  |  | Diagnostics of the breakdown should be verbally given to Arnot’s Services Manager within the first hour of arriving on-site. |  |
|  |  | Documented detailed diagnostics must be given to Arnot’s Services Manager by latest close of business the following day. |  |
|  |  | Repair time of the plant shall be within 48 hours as a worst-case scenario. Only under special conditions and on agreement with Arnot’s Services Manager can the defect be isolated and repaired beyond the 1-day time frame. |  |
|  |  | Tightening of cable connections that have loosened, as required |  |
|  |  | Repairs of MV and LV, AC as well as DC cable failures |  |
|  |  | Replacing blown fuses |  |
|  |  | Resetting tripped circuit breakers |  |
|  |  | Repairing lighting damage |  |
|  |  | Repairing equipment damaged by intruders or during module cleaning |  |
|  |  | Rectifying SCADA faults |  |
|  |  | Repairing mounting structure faults |  |
|  |  | Rectifying tracking system faults |  |
| 11 | Performance Monitoring, Evaluation & Optimisation | To optimise system performance, there is a need to ensure that the plant components function efficiently throughout the lifetime of the plant. Continuous monitoring of PV systems is essential to maximise the availability and yield of the system. The SCADA system is able to monitor the real-time efficiency and continuously compare it with the theoretical efficiency to assess if the system is operating optimally. This information shall be used by the contractor to establish the general condition of the system and schedule urgent repair or maintenance activities such as cleaning. | Continuously |
| 12 | Training | Host training workshops to enable Arnot Power Station to take the responsibilities of the new technology plant at the end of the 2-year term (should Arnot Power Station wish to do so). | 3 Monthly |

| Solar Plant Maintenance Activities |  |  |  |  |
| --- | --- | --- | --- | --- |
| No | Activity | Details |  | Frequency |
| 13 | Inventory | Availability of spares facilitate rapid response and PV plant serviceability. Hence a suitably stocked spares inventory is required. |  | Continuously |
|  |  | When spares are utilised, the contractor shall replenish the stock levels as soon as possible. |  |  |
|  |  | Consultation with manufacturers to detail the spare parts inventory, based upon estimated component lifetimes and failure rates shall be done. |  |  |
|  |  | Adequate supplies of the following components shall be held - as a minimum | Quantities |  |
|  |  | Mounting structure pieces | 10 |  |
|  |  | Junction combiner boxes | 3 |  |
|  |  | Fuses (MC4 connectors, breakers) | 10 |  |
|  |  | Circuit breakers | 10 |  |
|  |  | DC cabling components | 10 |  |
|  |  | AC cabling components | 10 |  |
|  |  | Communication equipment | 5 |  |
|  |  | Modules | 3 |  |
|  |  | Spare Inverters | 3 |  |

ANNEXURE C: Monthly Service Report Template

Eskom Holdings SOC Ltd

Arnot Power Station

Private Bag X2 Rietkuil

Arnot

1097

Contract Number 	:	TBA

Attention 		:	Services Manager

From 			:	TBA

Subject		: 	Monthly Service Report for Arnot Power Station PV Plant

Reporting Period	:  	Month of 2026

- Executive Summary / Introduction

A short introduction needs to be given regarding the activities.

- Background

  - Why the work needs to be done

  - Why this specific area was identified with reference to the bigger master plan or previous month’s roll-over / breakdown to be repaired / maintenance cycle / etc.

- Details

  - Insert what, why, when, and where of the specific activities / non-compliances /

Exactly describe the difference steps / actions that was completed.

  - Identify special fault-finding methods where necessary

  - Identify indicators to observe – e.g., water erosion, rain patterns, mole activities, Etcetera.

  - Refer to attachments (service sheets, other reports)

  - Include times where necessary

  - Include pitchers where necessary

  - Include tables where necessary

- Solutions

  - Where you able to complete all activities which was planned – if not, why

  - What is your specialist diagnosis of the system, why

  - Was the problem fixed (if any) temporarily / permeant

  - Note changes to documents and drawings, where applicable

  - Specify whether resources were used other than the normal shift hours (overtime/contractors/etc.)

- Recommendations

  - The section will close out the document

  - Is future upgrade / permanent work still required

  - Is a change in the works programme required and why.

- List of attachments

  - Add the list of all attachments and annexures to the report. As examples the following original documents must be attached – in order to supplement the comment s made in the other sections of the report above:

  - Procurement documentation

    - Quotations

    - Invoices

    - Purchases orders

    - Delivery Notes

    - Statements

  - PM’s and Work Orders

  - Safety Audits

  - Amendments drawings / Procedures

  - Toolbox Talks

  - Photographs

  - Accidents / Incidents Investigations reports

  - Breakdowns / Failures Reports

  - Daily reports

  - Training Certificates / Attendance forms

  - Meetings Minutes

  - Time and attendance registers

  - Etc.

Compiled By 	: Name

Signature 	:_______________________

Date		:______________________

ANNEXURE D: Contractor’s Schedule of equipment and tools

The Contractor shall provide a Schedule of equipment and tools, which will be used on this contract. The list will form part of the tender return schedules and is not

| Item No. | O&M categories of Tool and Equipment | Cleaning Tools | Inspection Tools |
| --- | --- | --- | --- |
| 1. | PV module inspection & cleaning equipment | Contractor to List | Contractor to List |
| 2. | Electrical testing & measurement equipment | Contractor to List DC Side (Modules & Strings) | Contractor to List AC Side (Inverters, Transformers, MV/LV Boards) |
| 3. | Scada / communications / control equipment (O&M) | Contractor to List |  |
| 4. | Mechanical & structural maintenance tools | Contractor to List |  |
| 5. | General maintenance & site upkeep equipment | Contractor to List |  |
| 6. | Safety, health & environment (she) equipment | Contractor to List |  |
| 7. | Drone & advanced inspection equipment | Contractor to List |  |
| 8. | Transport & handling equipment | Contractor to List |  |
| 9. | Documentation & software systems | Contractor to List |  |
| 10. | Emergency & contingency equipment | Contractor to List |  |

ANNEXURE E: Contractor’s Organogram Structure