PRELIMINARY REPORT

A Probabilistic Seismic Hazard Analysis for the

Bravo Power Station

BY:

A. Kijko

Report No. 2008 – 0013

© Council for Geoscience

DOCUMENT APPROVAL SHEET

| 1 | COUNCIL FOR GEOSCIENCE (Seismology Unit) | REFERENCE: CGS REPORT 2005-0118 |
| --- | --- | --- |
|  |  | REVISION |
|  |  | 0 |
| COPY No. | A Probabilistic Seismic Hazard Analysis for the Bravo Power Station | DATE OF RELEASE: |
|  |  | RESTRICTED |

| AUTHORS |  |  |  |
| --- | --- | --- | --- |
|  |  |  | APPROVED BY: |
| A. KIJKO |  |  | M. SINGH |
| ACCEPTED BY: |  |  | AUTHORISED BY: |
| Dr. A. CICHOWICZ |  |  | I. SAUNDERS |

| REVISION | DESCRIPTION OF REVISION | DATE | MINOR REVISIONS APPROVAL |
| --- | --- | --- | --- |

# CONFIDENTIALITY NOTICE

All information contained in this document and its appendices is privileged and confidential and is under no circumstances to be made known to any person or institution without the prior written approval of the Director: Council for Geoscience.

# ACKNOWLEDEMENTS

The following persons are thanked for their valued contribution (in alphabetical order):

Mayshree Singh		Diolinda Duarte		Jayson Ramperthap

# Executive Summary

A Probabilistic Seismic Hazard Analysis (PSHA) is performed for the proposed site of Eskom’s Bravo Power Station. All earthquakes located within a radius of 320 km from the proposed power station site were used for the assessment. The PSHA was performed using the The Cornell-McGuire procedure which can be broken down into two phases: 1) Spatial delineation of seismogenic sources within 320 km from the site and 2) integration of all possible earthquake scenarios from each source to obtain probabilities of exceedance of specified ground motion parameters.

Uniform horizontal ground acceleration spectra provides annual probability of exceedance relationships for ground motion at different frequencies. The service, abnormal and extreme curves show a spectral acceleration peak of approximately 0.13 g, 0.20 g and 0.30 g, at 20 Hz, respectively.

Note that this work looks strictly at ground motions that can be experienced at the site itself. Additional considerations should be given with regards to the potential for surface rupture and/or deformation at the site due to earthquakes and secondary effects of ground motion such as landslides and liquefaction

Uniform acceleration response spectra at the proposed power station site.

Table of Contents

CONFIDENTIALITY NOTICE	1

ACKNOWLEDEMENTS	1

Executive Summary	2

Table of Contents	Error! Bookmark not defined.

Definition of Terms, Symbols and Abbreviations	4

List of Figures	8

LIST OF TABLES……………………………………………………………………………….

1. Introduction	9

2. The SEISMIC ZONES AND THEIR PARAMETERS	10

2.1. Earthquake Catalogues used in the Analysis	11

3.THE SITE SPECIFIC HAZARD

3.1. The Calculation of PGA and Incorporation of Uncertainty	14

3.2. PGA Exceedance Probabilities and Mean Return Periods	15

3.3. Plots of PGA Exceedance Probabilities and Mean Return Periods	16

3.4. Uniform Acceleration Response Spectra	19

3.5. The Elastic Design Spectra	20

4. Conclusions	22

5. References	23

Appendix A: PSHA Methodology	36

Appendix A: Site-Specific Hazard Information File	36

# Definition of Terms, Symbols and Abbreviations

| Acceleration | The rate of change of particle velocity per unit time. Commonly expressed as a fraction or percentage of the acceleration due to gravity (g), where g = 9,81 m/s2. |
| --- | --- |
| Acceleration Response Spectra (ARS) | Spectral acceleration is the movement experienced by a structure during an earthquake. |
| Annual Probability of Exceedance | The probability that a given level of seismic hazard (typically some measure of ground motions, e.g., seismic magnitude or intensity), or seismic risk (typically economic loss or casualties) |
| Area-specific mean seismic activity rate (A) | Mean rate of seismicity for the whole selection area in the vicinity of the site for which the PSHA is performed. |
| Attenuation | A decrease in seismic-signal amplitude as waves propagate from the seismic source. Attenuation is caused by geometric spreading of seismic-wave energy and by the absorption and scattering of seismic energy in different earth materials. |
| Attenuation law (relationship) | A mathematical expression that relates a ground motion parameter, such as the peak ground acceleration, to the source and propagation path parameters of an earthquake such as the magnitude, source-to-site distance, fault type, etc. Its coefficients are usually derived from statistical analysis of earthquake records. It is a common engineering term for a ground motion relation. |
| b-value (b) | A coefficient in the frequency-magnitude relation, log N(m) = a – bm, obtained by Gutenberg and Richter (1941; 1949), where m is the earthquake magnitude and N(m) is the number of earthquakes with magnitude greater than or equal to m. Estimated b-values for most seismic zones fall between 0,6 and 1,1. |
| Capable fault | A mapped fault that is deemed a possible site for a future earthquake with magnitude greater than some specified threshold. |
| Catalogue | A chronological listing of earthquakes. Early catalogues were purely descriptive, i.e., they gave the date of each earthquake and some description of its effects. Modern catalogues are usually quantitative, i.e., earthquakes are listed as a set of numerical parameters describing origin time, hypocenter location, magnitude, focal mechanism, moment tensor, etc. |
| CGS | Council for Geoscience |
| Power Station ping | In vibration analysis, a term that indicates the mechanism for the dissipation of the energy of motion. Viscous Power Station ping, which is proportional to the velocity of motion and is described by linear equations, is used to define different levels of response spectra and is commonly used to approximate the energy dissipation in the lower levels of earthquake response. |
| Design Earthquake | The postulated earthquake (commonly including a specification of the ground motion at a site) that is used for evaluating the earthquake resistance of a particular structure. |
| Elastic design spectrum (or spectra) | The specification of the required strength or capacity of the structure plotted as a function of the natural period or frequency of the structure and of the Power Station ping appropriate to earthquake response at the required level. Design spectra are often composed of straight line segments (Newmark and Hall, 1982) and/or simple curves, for example, as in most building codes, but they can also be constructed from statistics of response spectra of a suite of ground motions appropriate to the design earthquake(s). To be implemented, the requirements of a design spectrum are associated with allowable levels of stresses, ductilities, displacements or other measures of response. |
| Earthquake | Ground shaking and radiated seismic energy caused most commonly by sudden slip on a fault, volcanic or magmatic activity, or other sudden stress changes in the Earth. |
| Epicenter | The epicenter is the point on the earth's surface vertically above the hypocenter (or focus). |
| Epicentral distance () | Distance from the site to the epicenter of an earthquake. |
| Fault | A fracture or fracture zone in the Earth along which the two sides have been displaced relative to one another parallel to the fracture. The accumulated displacement may range from a fraction of a meter to many kilometres. The type of fault is specified according to the direction of this slip. Sudden movement along a fault produces earthquakes. Slow movement produces aseismic creep. |
| Focal depth (h) | Focal depth is the vertical distance between the hypocentre and epicentre. |
| Frequency | The number of cycles of a periodic motion (such as the ground shaking up and down or back and forth during an earthquake) per unit time; the reciprocal of period. Hertz (Hz), the unit of frequency, is equal to the number of cycles per second. |
| Ground motion | The movement of the earth's surface from earthquakes or explosions. Ground motion is produced by waves that are generated by sudden slip on a fault or sudden pressure at the explosive source and travel through the earth and along its surface. |
| Ground motion parameter | A parameter characterizing ground motion, such as peak acceleration, peak velocity, and peak displacement (peak parameters) or ordinates of response spectra and Fourier spectra (spectral parameters). |
| Heterogeneity | A medium is heterogeneous when its physical properties change along the space coordinates. A critical parameter affecting seismic phenomena is the scale of heterogeneities as compared with the seismic wavelengths. For a relatively large wavelength, for example, an intrinsically isotropic medium with oriented heterogeneities may behave as a homogeneous anisotropic medium. |
| Hypocenter | The hypocenter is the point within the earth where an earthquake rupture starts. The epicenter is the point directly above it at the surface of the Earth. Also commonly termed the focus. |
| Hypocentral distance (r) | Distance from the site to the hypocenter of an earthquake. |
| Induced earthquake | An earthquake that results from changes in crustal stress and/or strength due to man-made sources (e.g., underground mining and filling of a high Power Station ), or natural sources (e.g., the fault slip of a major earthquake). As defined less rigorously, “induced” is used interchangeably with “triggered” and applies to any earthquake associated with a stress change, large or small. |
| Local Magnitude (ML) | A magnitude scale introduced by Richter (1935) for earthquakes in southern California. ML was originally defined as the logarithm of the maximum amplitude of seismic waves on a seismogram written by the Wood-Anderson seismograph (Anderson and Wood, 1925) at a distance of 100 km from the epicenter. In practice, measurements are reduced to the standard distance of 100 km by a calibrating function established empirically. Because Wood-Anderson seismographs have been out of use since the 1970s, ML is now computed with a simulated Wood-Anderson records or by some more practical methods. |
| Magnitude | In seismology, a quantity intended to measure the size of earthquake and is independent of the place of observation. Richter magnitude or local magnitude (ML) was originally defined in Richter (1935) as the logarithm of the maximum amplitude in micrometers of seismic waves in a seismogram written by a standard Wood-Anderson seismograph at a distance of 100 km from the epicenter. Empirical tables were constructed to reduce measurements to the standard distance of 100 km, and the zero of the scale was fixed arbitrarily to fit the smallest earthquake then recorded. The concept was extended later to construct magnitude scales based on other data, resulting in many types of magnitudes, such as body-wave magnitude (mb), surface-wave magnitude (MS), and moment magnitude (MW). In some cases, magnitudes are estimated from seismic intensity data, tsunami data, or duration of coda waves. The word “magnitude” or the symbol M, without a subscript, is sometimes used when the specific type of magnitude is clear form the context, or is not really important. |
| Maximum Regional Earthquake Magnitude (mmax) | Upper limit of magnitude for a given seismogenic zone or entire region. Also referred to as the maximum credible earthquake (MCE). |
| Operating Basis Event (OBE) | Event with an average return period in the order of 145 years i.e. 50 % probability of exceedance in 100 years. |
| Oscillator | In earthquake engineering, an oscillator is an idealized damped mass-spring system used as a model of the response of a structure to earthquake ground motion. A seismograph is also an oscillator of this type |
| Parameter of the distribution of ln(PGA) () |  = /c2 , where  = b ln(10) [see “b-value”] , and c2 is a coefficient related to the attenuation relationship. |
| Peak Ground Acceleration (PGA) | The maximum acceleration amplitude measured (or expected) of an earthquake. |
| Probabilistic Seismic Hazard Analysis (PSHA) | Available information on earthquake sources in a given region is combined with theoretical and empirical relations among earthquake magnitude, distance from the source and local site conditions to evaluate the exceedance probability of a certain ground motion parameter, such as the peak acceleration, at a given site during a prescribed period. |
| Response spectrum | The response of the structure to a specified acceleration time series of a set of single-degree-of-freedom oscillators with chosen levels of viscous damping, plotted as a function of the undamped natural period or undamped natural frequency of the system. The response spectrum is used for the prediction of the earthquake response of buildings or other structures. |
| Seismic Hazard | Any physical phenomena associated with an earthquake (e.g., ground motion, ground failure, liquefaction, and tsunami) and their effects on land use, man-made structure and socio-economic systems that have the potential to produce a loss. It is also used without regard to a loss to indicate the probable level of ground shaking occurring at a given point within a certain period of time. |
| Seismic Wave | A general term for waves generated by earthquakes or explosions. There are many types of seismic waves. The principle ones are body waves, surface waves, and coda waves. |
| Seismic zone | An area of seismicity probably sharing a common cause. |
| Seismogenic | Capable of generating earthquakes. |
| Site-specific mean activity rate (λS) | Mean activity rate of the selected ground motion parameter experienced at the site. |
| Strong ground motion | A ground motion having the potential to cause significant risk to a structure's architectural or structural components, or to its contents. One common practical designation of strong ground motion is a peak ground acceleration of 0.05g or larger. |

# List of Figures

Figure 1. Distribution of seismic events within a 320 km radius of the Bravo Power Station site and seismic zones used in the study. The zones are delineated by the mine related seismicity at Gauteng, (Johannesburg and Carletonville area), Klerksdorp and Welcom areas.

Figure 2.  The annual probability of exceedance of different PGA values.

Figure 3.  PGA values for probabilities of exceedance in 50, 100 and 1 000 years respectively.

Figure4.  The mean return period of earthquakes resulting in specified PGA’s at the site.

Figure 5.  Uniform acceleration response spectra at the future Station site, (a)  for 3 exceedance probabilities, namely 0.5 %, 0. 1 % and 0.01 %,  referred to as the service, abnormal and extreme curves, respectively and (b) for 7 mean return periods, namely 100, 200, 475,1,000, 10,000, 100,000 and 1,000,000 years

Figure 6.  5% damping Newmark-Hall acceleration design spectrum  for PGA at 0,12 g.

Appendix A.

Figure A1. Illustration of data which can be used by seismic hazard assessment code to obtainreccurence   parameters for the specified seismic source. The approach permits the combination of the largest earthquakes (prehistoric/paleo- and historic) data and complete (instrumental) data having variable threshold magnitudes. It accepts “gaps” (Tg) when records were missing or the seismic networks were out of operation. The procedure is capable to account for uncertainties of occurrence time of prehistoric earthquakes. Uncertainty in earthquake magnitude is also taken into account in that an assumption is made that the observed magnitude is true magnitude subjected to a random error that follows a Gaussian distribution having zero mean and a known standard deviation. (Modified after Kijko and Sellevoll, 1992)

List of Tables

Table.1 Division of the catalogue used in the analysis. mmin  = Level of Completeness; SE = standard error (assumed uncertainty in local Richter magnitude, ML , determination).

Table 2. Estimated recurrence parameters for each seismic zone. The value of the mean seismic activity rate  has been calculated for magnitude ML 4.0 and normalized for area of 0.2x0.2 degree.

# 1. Introduction

The Council for Geoscience (CGS) was requested by the Eskom Holdings Limited to provide probabilistic seismic hazard analysis (PSHA) at the proposed Bravo Power Station site. Information contained in the Earthquake Database of the CGS was used in the evaluation of the seismic hazard in this report.

Note that this work looks strictly at ground motions that can be experienced at the site itself. Additional considerations should be given with regards to the potential for surface rupture and/or deformation at the site due to earthquakes and secondary effects of ground motion such as landslides and liquefaction

The PSHA was performed using classical, Cornell-McGuire procedure (Cornell, 1968; McGuire, 1976), where the integration across the aleatory uncertainty in the PGA attenuation equation is an integral part of the methodology.

The procedure used in this seismic hazard assessment consists essentially of two steps. The first step is applicable to the seismic source zones (known also as seismogenic zones, seismic zones or in short, seismic sources) in the vicinity of the site, for which the seismic hazard assessment is required and it requires an estimation of the seismic source parameters. The second step is applicable to a specified site, and consists of assessing the site-specific parameters, which describe the amplitude distribution of two ground motion parameters, namely: peak ground acceleration (PGA) and uniform acceleration response spectra (ARS).

The PGA is the maximum acceleration of the ground shaking during an earthquake. Spectral acceleration is the movement experienced by a structure during an earthquake. The acceleration is expressed in units of gravity, g, which is equal to 9.81 m/s2.

The results are given in terms of mean return periods and probabilities of being exceeded, for specified earthquake magnitudes, PGA and ARS.

The procedure as applied in this work is described in Appendix A.

Appendix B shows the results of the calculations for the site of the future location of the Bravo Power station. It contains details of the computations, input data and respective hazard parameters. All results are based on the assumption that the proposed power station is founded on hard rock.

# 2. The Seismic Zones and their Parameters

In general, the division into seismic zones is based on the geotectonic, structural geological and earthquake occurrence information. In this study the area was divided into 3 seismic zones and background seismicity. Figure 1 illustrates the seismicity of the area surrounding the site and 3 seismic zones used in our study. Clearly, the selected seismic zones are delineated by the mine related seismicity at Gauteng, (Johannesburg and Carletonville area), Klerksdorp and Welkom areas.

Figure 1. Distribution of seismic events within 320 km radius of the Bravo Power Station site and seismic zones used in the study. The zones are delineated by the mine related seismicity at Gauteng, (Johannesburg and Carletonville area), Klerksdorp and Welkom areas.

Figure 1 shows the distribution of all known seismic events that occurred within a radius of 320 km from the future power station site, where the majority of events are located. Only events within a radius of 320 km from the power station site were used in the analysis, as only these events can be considered to contribute to the seismic hazard at the proposed power station site. Events at larger distances from the structure will not likely generate PGA’s large enough to be of engineering concern.

Each seismic zone shown in Figure 1 is described by set of 3 recurrence parameters: the mean seismic activity rate, , the Gutenberg-Richter parameter b and the maximum possible earthquake magnitude, mmax. The maximum possible earthquake magnitude is sometimes called the Maximum Credible Earthquake (MCE), and defined as an event with an annual probability of exceedance in the order of 10-3 -10-4, (Wieland, 2003) . The activity rate, , is the expected number of earthquakes of a given magnitude and stronger that will occur per unit time (e.g. per year). The Gutenberg – Richter b-value gives the slope of the frequency–magnitude curve and defines the ratio between the number of large and small earthquake occurrences. The maximum possible regional characteristic earthquake magnitude, mmax, is the upper limit of magnitude for a given seismogenic source zone

## 2.1. Earthquake Catalogues used in the Analysis

The catalogue used in the analysis spans a period of 200 years, from 1 January 1806 to 31 December 2006.The catalogue is divided into eight sub-complete parts. (Table 1).

Table.2 Division of the catalogue used in the analysis. mmin  = Level of Completeness; SE = standard error (assumed uncertainty in local Richter magnitude, ML , determination).

| Span | mmin | SE |
| --- | --- | --- |
| 1806 – 1905 | 5.9 | 0.3 |
| 1906 – 1910 | 5.3 | 0.2 |
| 1911 – 1950 | 4.9 | 0.2 |
| 1951-1970 | 4.6 | 0.2 |
| 1971-1980 | 4.0 | 0.1 |
| 1981-1990 | 3.8 | 0.1 |
| 1991-1995 | 3.2 | 0.1 |
| 1996-2002 | 3.0 | 0.1 |

## All together, 6097 events with ML magnitude equal to or larger than 3.0 were used for calculation of recurrence parameters in the three selected seismic zones. Table 2 summarizes estimated parameters for selected seismic zones. The mean seismic activity rate, , and the parameter b of the  Gutenberg-Richter relation were estimated by the maximum likelihood procedure. It was assumed, that for each seismic zone the value of the maximum possible earthquake magnitude, mmax is the same and was estimated as ML 5.6, by application of the K-S-B procedure (Kijko, 2004).

Table 2. Estimated recurrence parameters for each of the seismic zones. The value of the mean seismic activity rate  has been calculated for magnitude ML 4.0 and  normalized for area of 0.2x0.2 degree.

| ## Seismic Zone | ## Annual mean seismic activity rate  | ## b-value | ## mmax |
| --- | --- | --- | --- |
| ## “Gauteng” mining area (Johannesburg and Carletonville) | ## 0.0362 | ## 1.56 | ## 5.6 |
| ## Klerksdorp mining area | ## 0.219 | ## 1.18 | ## 5.6 |
| ## Welkom mining area | ## 0.0657 | ## 1.39 | ## 5.6 |

It must be noted that information on the seismic hazard threat to the power station would come from the expected PGA at the site and not necessarily the expected earthquake magnitude.

# 3. The Site-Specific Hazard

The site-specific parameters that describe the amplitude distribution of PGA and uniform ARS are estimated. The results are given in terms of exceedance probabilities and mean return periods of a specified PGA and ARS.

## 3.1. The Calculation of PGA and Incorporation of Uncertainty

The horizontal component of the PGA at the site of the power station was calculated, using a PGA attenuation curve of the form,

ln(a|m,r)=c1+c2⋅m+c34δr|rmax|rmax−|rmin|rmin+c42δrln|rmax|rmax|rmin|rmin−2δr  ,     (1a)

which is  the equation,

ln(PGA)=c1+c2⋅m+c3⋅r+c4⋅ln(r),      			                   (1b)

modified to account for uncertainties in hypocentral distance, r ,

where ,

r

r

r







min

,

,

and δr denotes the maximum possible error in the value of  r.

The tabulated values of PGA were obtained from Atkinson and Boore (1995, 1997), where ground acceleration is measured in units of gravity, [g], hypocentral distances r are measured in kilometres, m depicts moment magnitude and the coefficients in the attenuation equation (1b) are calculated as c1 = -2,68, c2 = 0,98, c3 = 0,0006 and c4 = -1,522. The above attenuation equation predicts the mean value of ln(PGA), with a standard deviation ln(PGA) equal to 0,61. The PGA values refer to sites of ordinary, competent rock characteristics. This limitation is due to the data having been obtained from seismological stations founded on hard rock.

## 3.3. PGA Exceedance Probabilities and Mean Return Periods

The values of the site-specific probabilistic seismic hazard assessment, in terms of horizontal PGA, are given in Appendix B. The columns [listed under the Results – Seismic Hazard Characteristics in terms of PGA section] represent site-specific PGA (in g), activity rate (indicated as LAMBDA), mean return period (in years), and probabilities of exceedance in 1, 50, 100 and 1 000 years.

Wieland (2003) suggests that for critical structures such as large dams the design PGA should be an event with a 10-4 probability of occurrence in one year. This level is reached at 0,12 g. (see also Figure 2).

Consider the probability of experiencing a PGA of engineering significance at the site of the power station. Following Appendix B, a horizontal PGA equal to 0,05 g is expected at the power station  site on average once every ≈ 172 years. The probability that this acceleration will be exceeded in any one year, as shown in Appendix B, is approximately 0,6 %. The probability that a PGA of 0,05 g will be exceeded in 100 years at the site of the power station  is approximately 44 %.

### 2.3.1. The Operating Basis Event (OBE)

The Operating Basis Event (OBE) is defined as the earthquake for which the structure is designed to remain operational. From an engineering point of view the OBE is more realistic, for it takes into account the maximum expected event in the lifetime of the structure. For critical structures such as large dams, Wieland (2003) proposes the OBE to be an event with an average return period in the order of 145 years (50 % probability of exceedance in 100 years). Accordingly the PGA for the OBE at the site of the Bravo power station is of the order of 0,05 g.

,.

## 3.4. Plots of PGA Exceedance Probabilities and Mean Return Periods

A graphical representation of the above PSHA is given in Figures 2, 3 and 4.

Figure 2 shows the probability for a given PGA to be exceeded in one year. Figure 3 shows the probability for a given PGA to be exceeded in 50, 100 and 1 000 years respectively. For instance, the probability for an earthquake causing a PGA exceeding 0.1 g at the site in 1 000 years is            ≈ 23 %.

Figure 4 shows the mean return periods of earthquakes resulting in specified PGA’s at the site. For instance, one can expect acceleration at the site of 0,1 g after every 3775 years on average.

Figure 2.  The annual probability of exceedance of different PGA values.

Figure 3.  PGA values for probabilities of exceedance in 50, 100 and 1 000 years respectively.

Figure4.  The mean return period of earthquakes resulting in specified PGA’s at the site.

## 3.5. Uniform Acceleration Response Spectra

The earthquake resistant design of a structure, such as a power station, is based on the adopted design earthquake. The design earthquake is merely used to determine the maximum value of PGA at the site and then using this value to acquire (scale) elastic design spectra known also as the Newmark-Hall design spectra or simply ‘engineering spectra’.

A different technique is used to assess the expected horizontal component of the vibration of the structure during a specified time interval. For this purpose so called uniform acceleration response spectrum (ARS) was calculated.

Figure 5a shows the uniform ARS calculated for the future power station site. Three annual exceedance probability curves, viz. 0,5 %, 0,1 % and 0,01 %, are shown in the figure, respectively. For critical structures as e.g. big dams, these are also referred to as the service, abnormal and extreme curves. For instance, the service, abnormal and extreme curves show a spectral of approximately 0,13 g, 0,20 g and  0,3 g, at 20 Hz, respectively. Figure 5b shows the uniform ARS for different return periods.

Figure 5.  Uniform acceleration response spectra at the future Station site, (a)  for 3 exceedance probabilities, namely 0.5 %, 0. 1 % and 0.01 %,  referred to as the service, abnormal and extreme curves, respectively and (b) for 7 mean return periods, namely 100, 200, 475,1,000, 10,000, 100,000 and 1,000,000 years

## 3.6. The Elastic Design Spectra

The elastic design spectrum characterises required strength or capacity of the structure. In this report, construction of the elastic design spectrum is based on formulas given by (Newmark and Hall, 1982).

Figure 6 represents the elastic pseudo-design spectrum for ground motions with PGA of 0.12 g at   5 % power Station site, as a function of the natural frequency of a system. The curve gives the median value of the spectral acceleration.

It is important to note that the systems of natural frequency of vibration between approximately 2 and 8 Hz exhibit an amplification of PGA of 2.7 (5 % damping). The design spectrum differs from the any single response spectrum in that it is an envelope of whole 	possible range of the response spectra from earthquakes producing the same value of the maximum credible PGA at the site. The elastic design spectrum is a basis for calculating the design force for single degree of freedom systems to be designed to remain elastic (Chopra, 1995).

Figure 6.  5% damping Newmark-Hall acceleration design spectrum  for PGA at 0.12 g.

# 4. Conclusions

The seismic hazard at the Bravo Power Station site in terms of expected PGA’s and ARS is summarised below.

The design PGA should be an event with a 10-4 probability of occurrence in one year. This level is reached at 0.12 g (see also Figure 2).

Through considering the design PGA, (an event with a 10-4 probability of occurrence in one year), a maximum credible horizontal PGA of 0.12 g was determined. The vertical-to-horizontal ground acceleration ratio can conservatively be taken as 0.6 (Ambraseys, 1995). This would imply a vertical PGA of ≈ 0.07 g.

A PGA of 0.05 g (a minimum acceleration that is considered hazardous to poorly built structures) has a mean return period equal to approximately 172 years, and a probability of exceedance in 100 years of 44 % at the site of the power station.

The effect of seismic sources activity within a radius of 320 km from the Power Station site was assessed in order to determine the horizontal component of PGA. The service, abnormal and extreme curves of uniform ARS show a peak of approximately 0.13 g, 0.20 g and 0.30 g at 20 Hz, respectively.

It should be emphasized that, in the above quantification of the seismic hazard, all the results are based on the assumption that the power station is founded on hard rock.

# 5. References

Ambraseys, N.N. (1995). The prediction of earthquake peak ground acceleration in Europe, Earthq. Eng. And Struct, Dynamics, 24, 467-490.

Atkinson, G.M. and Boore, D.M. (1995). Ground-motion relations for eastern North America, Bull. Seism. Soc. Am. 85, 17-30.

Atkinson, G.M. and Boore, D.M. (1997). Some comparisons between recent ground-motion relations, Seism. Res. Lett. 68, 24-40.

Chopra, (1995). Dynamics of Structures. Prentice Hall International, Inc. New Jersey.

McGuire, R.K. (1976). FORTRAN computer program for seismic risk analysis, U.S. Geol. Surv. Open-File Rept. 76-67.

Newmark, N.M., and Hall, W.J., Earthquake Spectra and Design, Earthquake Engineering Research Institute, Berkeley, Calif., (1982), pp. 29-37.

Wieland, M. (2003), Seismic aspects of Power Station s. Transactions of the International Commission on Large Power Station s, Q83. Vol. 3, 1243 – 1299, Montreal, Canada.

United States Committee on Large Power Plants (April 1999). Updated Guidelines for Selecting Seismic Parameters for Power Plants Projects.

# Appendix A: PSHA METHODOLOGY

## Introduction

This Appendix summarizes the main points of the procedure used for assessment of the seismic source recurrence parameters in case when the data are incomplete and uncertain. Use is made of the most common assumptions in engineering seismology that earthquake occurrences follow a Poisson process and that earthquake magnitudes follow a Gutenberg-Richter doubly-truncated distribution. Following this assumption the parameters obtained for each seismogenic source zone are: the mean seismic activity rate,  (which is a parameter of the Poisson distribution), the level of completeness of the earthquake catalogue, mmin, the maximum regional earthquake magnitude, mmax, and the Gutenberg-Richter parameter, b.  To assess the above parameters a seismic event catalogue containing origin times, size of seismic events and spatial locations is needed.

The maximum regional magnitude, mmax, is of paramount importance in this approach, therefore a statistical technique that can be used for evaluating this important parameter is presented.

## Estimation of the Seismic Source Recurrence Parameters – Bayesian Approach

This section gives an outline of the procedure used to determine the seismic source recurrence parameters: the mean seismic activity rate, , the Gutenberg-Richter parameter b and the maximum regional earthquake magnitude, mmax.

### Nature of Input Data

The lack or incompleteness of data in earthquake catalogues is a frequent issue in a statistical analysis of seismic hazard. Contributing factors include the historical and socio – economic context, demographic variations and alterations in the seismic network. Generally, the degree of completeness is a monotonically increasing function of time, i.e. the more recent portion of the catalogue has a lower level of completeness. The methodology makes provision for the earthquake catalogue to contain three types of data: firstly, very strong prehistoric seismic events (paleo-earthquakes), which usually occurred over the last thousands of years.  Secondly, the macro-seismic observations of some of the strongest seismic events that occurred over a period of the last few hundred years, and finally, complete recent data for a relatively short period of time.  The complete part of the catalogue can be divided into several sub-catalogues, each of which is complete for events above a given threshold magnitudemmini, and occurring in a certain period of time Ti where i = 1 , … , s and  s is the number of complete sub-catalogues. The approach permits ‘gaps’ (Tg) when records were missing or the seismic networks were out of operation. Uncertainty in earthquake magnitude is also taken into account in that an assumption is made that the observed magnitude is true magnitude subjected to a random error that follows a Gaussian distribution having zero mean and a known standard deviation. Figure 1 depicts the typical scenario confronted when conducting seismic hazard assessments.

Figure A 2. Illustration of data which can be used by seismic hazard assessment code to obtainreccurence   parameters for the specified seismic source. The approach permits the combination of the largest earthquakes (prehistoric/paleo- and historic) data and complete (instrumental) data having variable threshold magnitudes. It accepts “gaps” (Tg) when records were missing or the seismic networks were out of operation. The procedure is capable to account for uncertainties of occurrence time of prehistoric earthquakes. Uncertainty in earthquake magnitude is also taken into account in that an assumption is made that the observed magnitude is true magnitude subjected to a random error that follows a Gaussian distribution having zero mean and a known standard deviation. (Modified after Kijko and Sellevoll, 1992)

.

### Statistical Preliminaries

Basic statistical distributions and quantities utilised in the development of the methodology are briefly described in what follows.

The Poisson distribution is used to model the number of occurrences of a given earthquake magnitude or a given amplitude of a selected ground motion parameter being exceeded within a specified time interval.

pn|λ, t = PN=n|λ, t = λ tnn!e−λ t n = 0,1,2, ...  	 (1)

Note that λ here refers to the mean of the distribution, and describes the mean activity rate (mean number of occurrences).

The gamma distribution, given its flexibility, is used to model the distribution of various parameters in our approach and is given by,

fx = xq−1pqΓqe−p x, x>0 ,                          	(2)

where Γq is the gamma function defined as,

Γq = 0∞yq−1e−ydy , q>0,                                    	(3)

The parameters p and q are related to the mean μ, and variance σ2, of the distribution according to,

μx = qp ,                                                       	(4)

σx2 = qp2,                                                       	(5)

The coefficient of variation expresses the uncertainty related to a given parameter, and is given by,

COVx = σxμx,                                                      	(6)

thus describing the variation of a parameter relative to it’s mean value, with a higher value indicating a greater dispersion of the parameter.

### Estimation of the seismic source recurrence parameters

The standard assumption adopted is that the distribution of earthquakes with respect to their size obeys the classical Gutenberg-Richter relation,

logNm = a−b⋅m−mmin ,                                   	(7)

where Nm is the number of earthquakes of m≥mmin, occurring within a specified period of time,  and a and b are parameters.

Aki (1965) found that equation (7) implied a singly truncated exponential distribution of the form,

FMm = PM≤m =1−e−βm−mmin ,                                          	(8)

where β=bln10.

The earthquake occurrences over time in the given area are assumed to satisfy a Poisson process (1) having an unknown mean seismic activity rate λ.

The disregard of temporal variations of the parameters λ and b can lead to biased estimates of seismic hazard. An explicit assumption behind most hazard assessment procedures is that parameters λ  and b and remain constant in time. However, examination of most earthquake catalogues indicates that there are temporal changes of the mean seismic activity rate λ  as well as of the parameter b. For some seismic areas, the b-value has been reported to change (decrease/increase) its value before large earthquakes.  Usually, such changes are explained by the state of stress; the higher the stress, the lower the b-value.  Other theories connect the b-value with the homogeneity of the rock: the more heterogeneous the rock, the higher the b-value.  Finally, some scientists connect the fluctuation of the b-value with the seismicity pattern and believe that the b-value is controlled by the buckling of the stratum.  Whatever the mechanism, the phenomenon of b-value fluctuation is indubitable and well-known.  A wide range of international opinions concerning changes of patterns in seismicity, together with an extensive reference list, are found in a monograph by Simpson and Richards (1981) and in a special two issue of the Pure and Applied Geophysics, (Seismicity Patterns …, 1999; Microscopic and Macroscopic …, 2000). Treating both parameters λ  and  b as random variables modelled by respective gamma distributions allows us to appropriately account for the statistical uncertainty in these important parameters. In practice, the adoption of the gamma distribution does not really introduce much limitation, since the gamma distribution can fit a large variety of shapes. Combining the Poisson distribution (1) together with the gamma distribution (2) with parameters pλ and qλ, we obtain the probability related to a certain number of earthquakes, n, per unit time t, for randomly varying seismicity,

Pn|t = 0∞pn|λA,tfλA dλA  = Γn+qλn!Γqλpλt+pλqλtt+pλn,                              	(9)

where pλ= λ/σλ2, qλ= λ2/σλ2 and () is the Gamma function (3). λ denotes the mean of the distribution of λ.

Similarly, combining the exponential distribution (8) with the gamma distribution for  with parameters pβ and qβ, and normalising (e.g. Campbell 1982) upon introducing an upper limit mmax for the distribution of earthquake magnitudes, we obtain the CDF of earthquake magnitudes,

FMm|mmin = Cβ 1−pβpβ+m−mminqβ,                          	(10)

where pβ= β/σβ2and qβ= β2/σβ2. The symbol β denotes the mean value of parameter β, σβ denotes the standard deviation of βand the normalizing coefficient Cβ is given by,

Cβ = 1−pβpβ+m−mminqβ−1,                                   	(11)

Noting that qλ = λ⋅pλ and qβ = β⋅pβ, equations (9) and (10) may alternatively be written respectively as,

Pn|t = Γn+qλn!ΓqλqλλAt+qλqλλAtλAt+qλn,                      	(12)

and

FMm|mmin = Cβ 1−qβqβ+βm−mminqβ,                        	(13)

with

Cβ = 1−qβqβ+βmmax−mminqβ−1,                                 	(14)

Note that qβ= COVβ−12 and qλ= COVλ−12. Upon specification of the COV, the parameters λ and β, referred to as hyper-parameters of the respective distributions are estimated on the basis of observed data by applying the maximum likelihood procedure.

#### Extreme Magnitude Distribution as Applied to Prehistoric (Paleo) and Historic Events

Let us build the likelihood function of desired seismicity parameters θ = (λ,β), based on the prehistoric (paleo) and historic parts of the catalogue, containing the strongest events only. In this section we will only discuss the details of the likelihood function based on historic earthquakes, since except for a few details, the likelihood function based on prehistoric events is built in a similar manner.

By the Theorem of the Total Probability (see e.g. Cramér, 1961), the probability that in time interval t either no earthquake occurs, or all occurring earthquakes have magnitude not exceeding m, may be expressed as (Epstein and Lomnitz, 1966; Gan and Tung, 1983; Gibowicz and Kijko, 1994)

FMmaxm | m0 ,t = i=0∞Pi|t FMm | m i,                               	(15)

Relation (15) can be expressed in a much more simpler form (e.g. Campbell, 1982), which, in our notation, may be written as

FMmaxm | m0 , t = qλqλ + λ0 t 1−FMm | m0qλ,                             	(16)

In relations (15) and (16), m0 is the threshold magnitude for the prehistoric or historic part of the catalogue (m0  mmin). Magnitude mmin plays the role of the ‘total’ threshold magnitude and has a rather formal character.  The only restriction on the choice of its value is that mmin may not exceed the threshold magnitude of any part, prehistoric, historic or complete, of the catalogue.

It follows from relation (16) that the probability density function (PDF) of the largest earthquake magnitudes m within a period t is,

fMmax(m|m0,t)=λ0 tqλfM(m|m0)FMmax(m|m0,t)qλ+λ0 t[1−FM(m|m0)] ,                    	(17)

λ0 represents the mean of the distribution of the mean activity rate for earthquakes with magnitudes not less than m0 , and is given by,

λ0 =λA 1−FMm | m0 ,                                          	(18)

where λA,  as defined above,  is mean of the distribution of the mean activity rate corresponding to magnitude value mmin. fMm|m0 is the PDF of earthquake magnitudes.  Based on (13) and the definition of the probability density function, it takes the following form:

fMm = Cβ βqβqβ + βm−m0qβ+1,                               	(19)

After introducing the PDF (17) of the largest earthquake magnitude m within a period t, the likelihood function of unknown parameters θ, becomes:

L0θ | m0 , t0 , cov = i=1n0fMmaxm0i | m0 , ti ,                            	(20)

In order to build the likelihood function (20), three kinds of input data are required: m0, t, and cov, where m0 is vector of the largest magnitudes, t denotes vector of the time intervals within which the largest events occurred and vector cov = covλ , covβ, consists of the coefficients of variation (amount of dispersion (/ uncertainty) relative to the mean) of the unknown parameters θ = (λ,β).

#### Combination of Extreme and Complete Seismic Catalogues with Different Levels of Completeness

Let us assume that the third, complete part of the catalogue, can be divided into s sub-catalogues (Figure 1). Each of them has a span Ti and is complete starting from the known magnitudemmini.  For each sub-catalogue i, mi is used to denote ni earthquake magnitudes mij, where mij ≥ mmini, i = 1 , … , s, and j = 1 , … , ni. Let Liθ|mi denote the likelihood function of the unknown θ = (λ,β), based on the i-th complete sub-catalogue.  If the size of seismic events is independent of their number, the likelihood function Liθ|mi  is the product of two functions, Liλ|mi  and Liβ|mi.

The assumption that the number of earthquakes per unit time is distributed according to (12), means that Liλ|mi has the following form:

Liλ|mi = const⋅ λit+qλ−qλλitλit+qλni,                         	(21)

where const does not depend on λ and λi is the mean activity rate corresponding to the threshold magnitude mmini and is given by,

λi =λ 1−FMmmini | mmin,                                      	(22)

Following the definition of the likelihood function based on a set of independent observations, and (19), Liβ|mi takes the form,

Liβ|mi = Cβ β ni j=1ni1+βqβmij−mmini−qβ+1,                 	(23)

Relations (21) and (23) define the likelihood function of the unknown parameters θ = (λA,β)  for each complete sub-catalogue.

Finally, Lθ, the joint likelihood function based on all data, i.e. the likelihood function based on the whole catalogue, is calculated as the product of the likelihood functions based on prehistoric, historic and complete data.

The maximum-likelihood estimates of the required hazard parameters θ = (λ,β) , are given by the value of θ which, for a given maximum regional magnitude mmax, maximizes the likelihood function Lθ.  The maximum of the likelihood function is obtained by solving the system of two equations ∂ ℓ∂ λA = 0 and ∂ ℓ∂ β = 0, where ℓ = lnLθ.

A variance-covariance matrix,D θ, of the estimated hazard parameters, λandβ, is calculated according to the formula (Edwards, 1972):

Dθ = −∂2ℓ∂λ2∂2ℓ∂λ∂β∂2ℓ∂β∂λ∂2ℓ∂β2−1,                                         	(24)

where derivatives are calculated at the point λ = λand β = β.

### Estimation of the Maximum Regional Earthquake Magnitude mmax

Suppose that in the area of concern, within a specified time interval T, there are n main seismic events with magnitudes m1 , … , mn.  Each magnitude mi ≥ mmin (i = 1 , … , n), where mmin is a known threshold of completeness (i.e. all events having magnitude greater than or equal to mmin are recorded).  It is further assumed that the seismic event magnitudes are independent, identically distributed, random variables with CDF described by equation (13).

From the condition that compares the largest observed magnitude mmaxobs and the maximum expected magnitude during a specified time interval T, we obtain the maximum regional magnitude mmax (Kijko and Graham, 1998; Kijko, 2004)

mmax = mmaxobs + δ1/qexpnrq/1−rqβΓ−1/q , δ rq − Γ−1/q , δ,            	(25)

where δ=nCβ and Γ is the complementary incomplete gamma function.  The approximate variance of the above estimator is equal to (Kijko, 2004)

σmmax2 ≃ σM2 + δ1/qexpnrq/1−rqβΓ−1/q , δ rq − Γ−1/q , δ2,              	(26)

where σMis the standard error in determination of the largest observed magnitude mmaxobs.

## References to Methodology Description

Aki, K. (1965). Maximum likelihood estimate of b in the formula log N = a – bM and its confidence limits, Bull. Earthq. Res. Inst.., Univ Tokyo 47, 237-239.

Ambraseys, N.N. (1995). The prediction of earthquake peak ground acceleration in Europe, Earthquake Eng. Struct. Dyn. 24, 467-490.

Atkinson, G.M. and D.M. Boore, (1997). Some comparisons between recent ground-motion relations, Seism. Res. Lett. 68, 24-40.

Campbell, K.W. (1982). Bayesian analysis of extreme earthquake occurrences. Part I.  Probabilistic hazard model, Bull. Seism. Soc. Am., 72, 1689-1705.

Cornell, C.A. (1968). Engineering seismic risk analysis, Bull. Seism. Soc. Am. 58, 1583-1606.

Cornell, C.A. (1971). Bayesian statistical decision theory and reliability-based design,  Proceedings of the International Conference on Structural Safety and Reliability,  A.M. Freudenthal, Editor, April 9-11, 1969, Washington, D.C., Smithsonian  Institute, 47-66.

Cramér, H. (1961). Mathematical Methods of Statistics, Princeton University Press. Princeton.

Edwards, A.W.F. (1972). Likelihood, Cambridge University Press, New York, p. 235.

Epstein, B., and C. Lomnitz (1966). A model for occurrence of large earthquakes.,  Nature, 211, 954-956.

Gan, Z.J. and C.C. Tung (1983). Extreme value distribution of earthquake magnitude, Phys. Earth Planet. Inter. 32, 325-330.

Gibowicz, S.J. and A. Kijko, (1994). An Introduction to Mining Seismology, Academic Press, San Diego.

Kijko, A. (2004), Estimation of the maximum earthquake magnitude mmax.  Pure Appl. Geophys,, 161, 1-27.

Kijko, A. and G. Graham, (1998). "Parametric-Historic" procedure for probabilistic seismic hazard analysis. Part I: Assessment of maximum regional magnitude mmax, Pure Appl. Geophys, 152, 413-442.

Kijko, A. and M.A. Sellevoll, (1992). Estimation of earthquake hazard parameters from  incomplete data files. Part II. Incorporation of magnitude heterogeneity. Bull.  Seism. Soc. Am. 82, 120-134.

Microscopic and Macroscopic Simulation: Towards Predictive Modelling of the Earthquake Process, Editors: P. Mora, M. Matsu’ura, R. Madariaga and J-B. Minster, Pure and Applied Geophysics, 157, pp. 1817-2383, 2000.

Seismicity Patterns, their Statistical Significance and Physical Meaning, Editors: M. Wyss, K. Shimazaki and A. Ito, Pure and Applied Geophysics, 155, pp. 203-726, 1999

Simpson, D.W., and P.G. Richards (1981). Earthquake Prediction, An International Review.   Maurice Ewing series IV, Eds: D. W. Simpson, and P.G. Richards. American  Geophysical Union, Washington, D.C., 680 pp.

# Appendix B: Site-Specific Hazard Information File

File       : HS_info_Bravo_PS.txt

Created on : 14-Jan-2008 12:09:45

PROGRAM NAME     : HS_C-McG (H = Hazard; S = Site; C = Cornell; McG = McGuire)

WRITTEN          : 15 SEP 2007 by A.K.

REVISED          : 27 SEP 2007 by A.K.

: 30 SEP 2007 by A.K.

: 01 OCT 2007 by A.K.

VERSION          : 1.02

For more information, contact A.Kijko or M.Bejaichund or J.Ramperthap,

Council for Geoscience, Geological Survey of South Africa

Private Bag X112, Pretoria 0001, South Africa.

Phone  :  +(27) (0) 12 841-1201 or 841-1454 or 841-1180

Fax    :  +(27) (0) 12 8411424

E-mail :  kijko@geoscience.org.za    (A.K.)

mayshree@geoscience.org.za (M.B.)

jasonr@geoscience.org.za   (J.R.)

==========================================================================

PROBABILISTIC SEISMIC HAZARD ASSESSMENT FOR A SELECTED SITE BY THE CORNELL-McGUIRE PROCEDURE

THE APPLIED METHODOLOGY IS DESCRIBED IN THE DOCUMENT:

"Recommendations for Probabilistic Seismic Hazard Analysis:

Guidance on Uncertainty and Use of Experts",

Prepared by:

Senior Seismic Hazard Analysis Committee (SSHAC),

R.J. Budnitz (Chairman), G. Apostolakis, D.M. Boore, L.S. Cluff,

K.J. Coppersmith, C.A. Cornell, and P.A. Morris.

Lawrence Livermore National Laboratory.

Prepared for:

U.S. Nuclear Regulatory Commission, U.S. Department of Energy and

Electric Power Research Institute.

NUREG/CR-6372, UCRL-ID-122160, vol.1, April 1997

THE CODE REQUIRES TWO INPUT FILES:

FILE CONTAINING SITE-SPECIFIC INFORMATION:

------------------------------------------

- Site coordinates, LATITUDE & LONGITUDE [DEG]

- MINIMUM VALUE OF ANNUAL PROBABILITY OF EXCEEDANCE of PGA for which

PSHA calculations are to be performed. Suggested values:

for nuclear facilities, between 10^(-6) and 10^(-4),

for large water reservoirs/dams between 10^(-4) and 10^(-3).

- 3 TIME INTERVALS for which PSHA will be performed.

Suggested values: 50, 100 and 1000 years.

- Parameter controlling the ACCURACY of numerical integration. If its

value = 1, the accuracy of integration is LOW, but computation time is SHORT.

If its value = 2, accuracy of integration is MODERATE, but computation

time is LONGER. If its value is 3, accuracy of integration is

HIGHEST, but computations require SIGNIFICANTLY more time.

- Parameter providing provision for increase/decrease of future

seismicity.

- Two parameters controlling UNCERTAINTY of the assumed seismicity model.

First parameter controls uncertainty of b-value in the FREQUENCY-

MAGNITUDE,

Gutenberg-Richter relation. Second parameter controls uncertainty

of the level of seismicity described by the mean activity rate LAMBDA.

- Parameter controlling predicted value of Ground Motion.

If its value is = 1, in all calculations the MEAN value of

ln(Ground Motion) is used. If its value is = 2, the predicted,

mean value of ln(Ground Motion) is increased by its STANDARD DEVIATION

FILE CONTAINING INFORMATION ON SEISMIC SOURCES IN THE VICINITY OF THE SITE

--------------------------------------------------------------------------

Each seismic source is described by 7 parameters:

(1) latitude [DEG], (2) longitude [DEG], (3) depth [KM] of seismic

source,

(4) Mean Activity Rate LAMBDA, (5) b-value of the frequency-magnitude

Gutenberg-Richter relation, (6) minimum magnitude Mmin, and

(7) MAXIMUM, seismic source-characteristic EQ-e magnitude Mmax.

PROBABILISTIC SEISMIC HAZARD ASSESSMENT BY CORNELL-McGUIRE PROCEDURE

======================================================================

The applied approach takes into account ground motion variability

by integrating across the scatter in the attenuation equation

NAME OF THE SITE: Bravo Power Station

ATTENUATION MODEL: MODYFIED, ATKINSON-BOORE (1997)

===================================================

ln[a(f)] = c1 + c2 * mag + c3 * r + c4 * ln(r) + c5 * p WHERE:

a         = PGA or SPECTRAL ACCELERATION IN UNITS OF [g]

f         = GROUND MOTION FREQUENCY [Hz]

mag       = EARTHQUAKE MAGNITUDE

r         = HYPOCENTRAL DISTANCE, [KM]

p         = IF p = 1, ln(a) = MEAN[ln(a)] + SD[ln(a)]

c1,...,c5 = COEFFICIENTS, WHERE c5 IS SD OF ln(a)

IF a = PGA, f = 99.9

ATTENUATION COEFFICIENTS

==============================

Freq. (Hz)        c1         c2        c3        c4        c5

---------------------------------------------------------------

0.5        -10.798      1.614     0.0042    -1.250     0.610

1.0         -9.213      1.531     0.0040    -1.237     0.610

2.0         -7.280      1.393     0.0032    -1.228     0.610

3.0         -5.927      1.276     0.0028    -1.259     0.610

5.0         -4.380      1.123     0.0021    -1.283     0.610

7.9         -3.453      1.042     0.0006    -1.279     0.610

10.0         -3.123      1.039     0.0002    -1.324     0.610

13.0         -2.749      0.983    -0.0011    -1.283     0.610

20.0         -2.346      0.968    -0.0033    -1.289     0.610

99.9         -2.682      0.980     0.0006    -1.522     0.610

SITE COORDINATES (LATITUDE)                = -25.550 [DEG]

SITE COORDINATES (LONGITUDE)               = 28.570 [DEG]

MINIMUM ANNUAL PROBABILITY OF EXCEEDANCE   = 1.000e-004 [DEG]

PSHA IS CALCULATED FOR TIME INTERVALS      = 50  100 and 1000 YEARS

ACCURACY OF NUMERICAL INTEGRATION: MEDIUM

MAGNITUDE INTEGRATION INTERVAL   = 0.25

PROVISION FOR INDUCED SEISMICITY: REQUIRED

MULTIPLICATIVE FACTOR OF LAMBDA = 1

MODEL UNCERTAINTY OF THE b-VALUE              = 25  [per cent]

MODEL UNCERTAINTY OF THE SITE-SPECIFIC LAMBDA = 25  [per cent]

ALL CALCULATIONS ARE PERFORMED FOR MEAN VALUE OF ln[Ground Motion]

NAME OF INPUT FILE WITH PARAMETERS OF SEISMIC SOURCES: ss.txt

PARAMETERS OF SUB-SEISMIC SOURCES

==================================

SOURCE   LAT[DEG]  LON[DEG]  DEPTH[KM]  b-value  LAMBDA   Mmin   Mmax

---------------------------------------------------------------------

1      -25.394    28.987     10.0       3.00    0.03    0.87  6.410

2      -25.201    29.503     10.0       3.00    0.08    0.86  6.440

3      -24.988    30.074     10.0       3.00    0.11    0.83  6.440

4      -24.771    30.655     10.0       3.00    0.16    0.80  6.440

5      -24.552    31.241     10.0       3.00    0.19    0.82  6.440

6      -25.174    28.743     10.0       3.00    0.02    0.88  6.440

7      -24.709    28.956     10.0       3.00    0.07    0.91  6.440

8      -24.193    29.193     10.0       3.00    0.07    0.87  6.440

9      -23.669    29.434     10.0       3.00    0.09    0.86  6.440

10      -23.141    29.676     10.0       3.00    0.09    0.90  6.490

11      -25.174    28.397     10.0       3.00    0.02    0.87  6.390

12      -24.709    28.184     10.0       3.00    0.06    0.85  6.440

13      -24.193    27.947     10.0       3.00    0.09    0.87  6.490

14      -23.669    27.706     10.0       3.00    0.12    0.93  6.490

15      -23.141    27.464     10.0       3.00    0.13    0.93  6.490

16      -25.394    28.153     10.0       3.00    0.02    0.85  6.390

17      -25.201    27.637     10.0       3.00    0.06    0.82  6.390

18      -24.988    27.066     10.0       3.00    0.13    0.88  6.420

19      -24.771    26.485     10.0       3.00    0.27    0.88  6.420

20      -24.552    25.899     10.0       3.00    0.33    0.92  6.330

21      -25.706    28.153     10.0       3.00    0.03    0.85  6.390

22      -25.899    27.637     10.0       3.00    0.07    0.85  6.390

23      -26.112    27.066     10.0       3.00    0.16    0.81  6.390

24      -26.329    26.485     10.0       3.00    0.31    0.84  6.420

25      -26.548    25.899     10.0       3.00    0.24    0.86  6.410

26      -25.926    28.397     10.0       3.00    0.03    0.86  6.390

27      -26.391    28.184      2.5       3.00   14.38    1.56  5.600

28      -26.907    27.947     10.0       3.00    0.13    0.84  6.390

29      -27.431    27.706     10.0       3.00    0.17    0.86  6.390

30      -27.959    27.464     10.0       3.00    0.29    0.81  6.390

31      -25.926    28.743     10.0       3.00    0.03    0.84  6.390

32      -26.391    28.956     10.0       3.00    0.09    0.83  6.390

33      -26.907    29.193     10.0       3.00    0.15    0.85  6.390

34      -27.431    29.434     10.0       3.00    0.21    0.85  6.390

35      -27.959    29.676     10.0       3.00    0.27    0.84  6.390

36      -25.706    28.987     10.0       3.00    0.03    0.85  6.390

37      -25.899    29.503     10.0       3.00    0.09    0.87  6.410

38      -26.112    30.074     10.0       3.00    0.13    0.87  6.430

39      -26.329    30.655     10.0       3.00    0.16    0.83  6.430

40      -26.548    31.241     10.0       3.00    0.20    0.82  6.430

SOURCE    HYP.DIS.[KM]   LAMBDA(effective)  Max(PGA)[g]

-----------------------------------------------------------

1          46.37           0.03            0.109

2         101.87           0.08            0.035

3         163.82           0.11            0.018

4         227.07           0.16            0.011

5         291.00           0.19            0.008

6          46.34           0.02            0.113

7         101.68           0.07            0.035

8         163.64           0.07            0.018

9         226.71           0.09            0.011

10         290.31           0.09            0.008

11          46.34           0.02            0.107

12         101.68           0.06            0.035

13         163.64           0.09            0.019

14         226.71           0.12            0.012

15         290.31           0.13            0.008

16          46.37           0.02            0.107

17         101.87           0.06            0.033

18         163.82           0.13            0.017

19         227.07           0.27            0.011

20         291.00           0.33            0.007

21          46.32           0.03            0.107

22         101.62           0.07            0.034

23         163.17           0.16            0.017

24         225.81           0.31            0.011

25         288.94           0.24            0.008

26          46.32           0.03            0.107

27         101.12          14.38            0.016

28         163.37           0.13            0.017

29         226.19           0.17            0.011

30         289.46           0.29            0.008

31          46.32           0.03            0.107

32         101.58           0.09            0.034

33         163.37           0.15            0.017

34         226.19           0.21            0.011

35         289.46           0.27            0.008

36          46.32           0.03            0.107

37         101.62           0.09            0.034

38         163.17           0.13            0.018

39         225.81           0.16            0.011

40         288.94           0.20            0.008

Max EXPECTED PGA AT THE SITE = 0.113 [g] (FROM SEISMIC SOURCE #6)

SEISMIC HAZARD

==========================================================

PGA[g]  Lambda[EQ/Y]     RP[Y]         Prob(T = 1  50  100  1000 [Y])

0.010   1.3743e+000   7.2763e-001   0.746988 1.000000 1.000000 1.000000

0.020   1.6351e-001   6.1157e+000   0.150844 0.999719 1.000000 1.000000

0.030   4.0042e-002   2.4974e+001   0.039251 0.864950 0.981761 1.000000

0.040   1.3890e-002   7.1993e+001   0.013794 0.500681 0.750681 0.999999

0.050   5.8025e-003   1.7234e+002   0.005786 0.251831 0.440244 0.996980

0.060   2.7264e-003   3.6678e+002   0.002723 0.127437 0.238633 0.934545

0.070   1.3941e-003   7.1730e+002   0.001393 0.067332 0.130130 0.751948

0.080   7.6147e-004   1.3132e+003   0.000761 0.037358 0.073320 0.533021

0.090   4.3899e-004   2.2779e+003   0.000439 0.021710 0.042950 0.355314

0.100   2.6488e-004   3.7753e+003   0.000265 0.013157 0.026141 0.232704

0.110   1.6623e-004   6.0159e+003   0.000166 0.008277 0.016485 0.153145

0.120   1.0795e-004   9.2636e+003   0.000108 0.005383 0.010737 0.102327

0.130   7.2254e-005   1.3840e+004   0.000072 0.003606 0.007199 0.069705