TABLE 12

Assessment of founding conditions and typical solutions for specific heavily loaded structures, based on boreholes beneath or near the respective structures

| Structure | BH and collar elevation | General geology | Depth to rock and elevation | Depth to rock below terrace | Foundation assessment |
| --- | --- | --- | --- | --- | --- |
| Turbines, Turbine Hall and Auxiliary Bay | bh32 1508,373 | Dwyka tillite | 6m 1502.373 | 0,4m | Spread or raft foundations on rock at a nominal depth below terrace level. |
|  | BH37 1510.202 | Dwyka shale | 5,45m 1504.752 | 0,0m |  |
|  | BH38 1508.177 | Dwyka tillite | 5,22m 1502,957 | 0,1m |  |
|  | BH39 1504,267 | Rayton shale | 1,0m 1503,267 | 0,0m |  |
|  | BH40 1500,812 | Rayton shale | 0,42m 1500,392 | 2,4m | Excavate to rock and use spread or raft foundations |
|  | BH41 1497,728 | Diabase | 7,5m 1490,228 | 12,5m | Piled foundations |
| Generators | BH44 1510,313 | Dwyka tillite | 3,75m 1506,563 | 0,0m | Spread or raft foundations on rock at a nominal depth below terrace level. |
|  | BH45 1509,681 | Dwyka shale | 3,57m 1506,611 | 0,0m |  |
|  | bh38 1507,958 | Rayton shale | 4,0m 1503,958 | 0,0m |  |
|  | bh54 1502,392 | Rayton shale | 1,7m 1500,692 | 2,1m | Excavate to rock and use spread or raft foundations |
| Boilers | bh32 1508,373 | Dwyka tillite | 6,0m 1502,373 | 0,4m | Excavate to rock and use spread or raft foundations |
|  | bh48 1501.176 | Rayton shale | 0,4m 1500,776 | 2,0m |  |
|  | BH35 1496,511 | Diabase | 3,2m 1493.31 | 9,5m | Piled foundations |
|  | bh41 1497,649 | Diabase | 9,22m 1488,429 | 14,4m |  |
| Air cooled Condensers | bh45 1507,757 | Dwyka tillite | 5,6m 1502,157 | 0,6m | Excavate to rock and use spread or raft foundations |
|  | bh46 1507,213 | Rayton shale | 6,08m 1501,677 | 1,1m |  |
|  | bh61 1500,185 | Rayton shale | 4,25m 1495,935 | 6,9m | Piled foundations |
|  | BH56 1497.688 | Diabase | 2,59m 1495,098 | 7,7m | Piled foundations |
| Chimney | BH11 ? | Dwyka siltstone | 4,5m ? | ? | Piled foundations. Boreholes indicate variable founding conditions for a raft foundation. |
|  | BH12 1511,305 | Dwyka shale | 13,05m 1497,805 | 5,0m |  |
| Chimney | BH13 1498,247 | Rayton shale | 0,3m 1497,47 | 4,9m | Piled foundations. Piling conditions appear to be straightforward. Boreholes indicate that it should be possible to form a socket to resist horizontal and tension loads |
|  | BH14 1497,367 | Rayton shale | 1,12m 1496,247 | 6,6m |  |