TABLE 13

Assessment of founding conditions and typical solutions for specific moderately loaded structures, based on boreholes beneath or near the respective structures

| Structure | BH and collar elevation | General geology | Depth to residual soils(S) and rock (R) and elevation | Depth to residual soils(S) and rock (R) below terrace | Foundation assessment |
| --- | --- | --- | --- | --- | --- |
| Demineralized water tanks | BH50 1505,89 | Dwyka siltstone | S – 1,1m 1504,79 R - 5,33m 1498,56 | S – 0,0m R – 4,24m | Spread or raft foundation at a nominal depth on the residual soils. Piled foundations only if settlements are not acceptable |
|  | PB04 1508 |  | S – 1,25m 1506,75 R – not proven | S – 0,0m R – not proven |  |
| Water treatment plant | bh21 1506,618 | Dwyka tillite | S – 0,6m 1506,018 R – 10,8m 1495,818 | S – 0,0m R – 7,0m | Spread or raft foundation at a nominal depth on the residual soils. Piled foundations only if settlements are not acceptable |
|  | PB05 1506 |  | S – 0,9m 1505,1 R – not proven | 0,0 |  |
|  | bh29 1506,338 |  | S – 1,15m 1505,188 R – 13,25m 1493,088 | S – 0,0m R – 9,7m |  |
| Waste water treatment plant | BH64 1502,069 | Dwyka shale | S – 2,1m 1499,969 R – 5,65m 1496,419 | S – 2,8m R – 6,4m | Spread or raft foundations taken through the fill to the residual soil. Placement of a high quality soil or rock fill in this area and place foundations in the fill. Piled foundations if settlements are not acceptable. |
|  | PB03 1501 |  | S – 1.5m 1499,5 R – not proven | S – 3,3m R – not proven |  |
| Auxiliary cooling plant | BH42 1493,508 | Diabase | S – 1,0m 1492,508 R – 1,65m 1491,858 | S – 10,3m R – 10,9m | Piled foundations |
| Auxiliary cooling plant | BH43 1508,660 | Dwyka tillite | S – 0,75m 1507,91 R – 10,25m 1498,41 | S – 0,0m R – 4,4m | Spread or raft foundation at a nominal depth on the residual soils. Piled foundations only if settlements are not acceptable |
| Fly ash conditioning plant Limestone silo Water tanks Auxiliary building | bh28 1490,398 | Diabase | S – 1,0m 1489,398 R – 5,02m 1485,378 | S - 13,4m R – 17,4m | Piled foundations |
|  | BH9 1493,874 |  | S – 0,6m 1493,274 R – 8,5m 1485,374 | S – 9,5 R – 17,4 |  |
|  | BH10 1491,020 |  | S – 0,73m 1490,290 R – 5,7m 1485,320 | S – 12,5m R – 17,5m |  |