# Table 7

PROJECT BRAVO – PRESSURES FOR HEAVY STRUCTURES*

| Item | Footing size (m) | Pressure (kPa) |
| --- | --- | --- |
| Turbines | 20 x 35 raft | 600 |
| Generator transformers | 5 x 5 | 600 |
| Turbine hall Auxiliary bay | 3 x 3 | 1000 |
| Boilers | 20 x 20 raft or 3 x 3 | 300 800 |
| Air cooled condensers | 7 x 7 raft | 600 |
| Chimneys | 28 x 28 raft | 1000 |

MODERATELY LOADED STRUCTURES

Demineralized water tanks			35 dia. raft		300

Water treatment plant				10 x 10 rafts		300

Waste water treatment plant			20 x 20 rafts		300

Auxiliary cooling plant		a)	16 x 16 raft		300

b)	20 x 20 raft		200

c)	22 x 22 raft		160

Fly ash conditioning plant		a)	16 dia. raft		400

b)	20 dia. raft		260

*  max. tolerable differential settlement 10 mm or less, but less than 2 mm for turbines

## TABLE 8

YOUNG’S MODULUS & POISSON’S RATIO

DWYKA TILLITE

(with some siltstone & sandstone)

| Consistency | Goodman Jack E(GPa) | Lab. E*(GPa) | Lab * |
| --- | --- | --- | --- |
| Stiff residual | 0.0215-0.0443 (0.0329 N=2)¥ | - | - |
| Soft rock | 0.31 – 2.0 (0.88 N = 16)† | 0.5 – 6.8 (3.4 N=7) | 0.10 - 0.26 (0.19) |
| Moderately hard rock | 1.12 – 9.28 (3.99 N = 11) | 6.2 (N = 1) | 0.14 |
| Hard rock | 6.57 -20.54 (10.01 N = 8) | 12.4-22.4 (17.4 N=2) | 0.13- 0.23 (0.18) |

¥   from plate-bearing tests

*  secant value at 50 %  UCS

†   value in brackets = mean; N = number of results

## TABLE 9

YOUNG’S MODULUS & POISSON’S RATIO

DWYKA  SHALE

| Consistency | Goodman Jack E(GPa) | Lab. E*(GPa) | Lab * |
| --- | --- | --- | --- |
| Stiff residual | 0.0149-0.0221 (0.0185 N=2)¥ | - | - |
| Very soft rock | 1.23 (N = 1)† | 0.4-2.3 (1.35 N=2) | 0.13-0.21 (0.17) |
| Soft rock | 0.19-1.69 (1.07 N=7) | 1.3-3.2 (2.1 N=4) | 0.15-0.19 (0.18) |
| Moderately hard rock | 0.93 (N=1) | 1.2 (N=1) | 0.21 |

¥   from plate-bearing tests

*  secant value at 50 %  UCS

†   value in brackets = mean; N = number of results

## TABLE 10

YOUNG’S MODULUS & POISSON’S RATIO

RAYTON  SHALE

| Consistency | Goodman Jack E (GPa) | Lab. E*(GPa) | Lab * |
| --- | --- | --- | --- |
| Very stiff residual | 0.0452 (N=1)¥ | - | - |
| Soft rock | 0.42-1.62 (0.96 N=3)† | - | - |
| Moderately hard rock | 0.78-3.11 (1.53 N=13) | 3.9-11.7 (7.8 N=2) | 0.13-0.17 (0.15) |
| Hard rock | 1.0-7.59 (4.35 N=10) | 3.0-3.2 (3.1 N=2) | 0.05 |

¥   from plate-bearing tests

*  secant value at 50 %  UCS

†   value in brackets = mean; N = number of results

## TABLE  11

YOUNG’S MODULUS & POISSON’S RATIO

DIABASE

| Consistency | Goodman Jack E (GPa) | Lab. E* (GPa) | Lab * |
| --- | --- | --- | --- |
| Firm to stiff residual residual | 0.0221 (N = 1)¥ | - | - |
| Very hard rock | 12.92-106.42 (40.06 N=10)† | 88.9 (N=1) | 0.28 |

¥   from plate-bearing tests

*  secant value at 50 %  UCS

†   value in brackets = mean; N = number of results